## Sheet 1
Compiled Date / Time | Compiler | Warning (no score) | Warning (neg loss) | Name of City / Utility | City / Town | State | Country | Contact Name | Contact Email Address | Telephone | Report Year | CY/FY | Reporting Period | Audit Prep Date | Units | PWS/OtherID | Water Audit Validator Name | Water Audit Validator Email | Water System Service Population | Water System Structure | Water Type | Volume From Own Sources | Volume From Own Sources MMEA | Water Imported | Water Imported MMEA | Water Exported | Water Exported MMEA | Water Supplied | Billed Metered | Billed Unmetered | Unbilled Metered | Unbilled Unmetered | Unbilled Unmetered Default Used | Authorized Consumption | Water Losses | Unauthorized Consumption | Unauthorized Consumption Default Used | Customer Metering Inaccuracies | CMI Percent | Systematic Data Handling Errors | Systematic Data Handling Errors Default Used | Annual Volume of Apparent Losses | Annual Volume of Real Losses | Non Revenue Water | Length of Mains | Number of Active and Inactive Service Connections | Service Connection Density | Customer meters located at the Curbstop/ property line | Average length of customer service line | Average Operating Pressure | Total Annual Cost of Operating Water System | Customer Retail Unit Cost | Customer Retail Units | Variable Production Cost | Unavoidable Annual Real Losses (UARL) vol/Yr | Unavoidable Annual Real Losses (UARL) vol/conn/day | Annual Volume of AL2 | Annual Volume of RL3 | Annual Volume of Unbilled Auth. Consumption | Annual Volume of NRW | Annual Cost of Apparent Losses | Annual Cost of Real Losses | Annual Cost of Unbilled Auth. Consumption | Annual Cost of NRW | Value Applied to Real Losses (VPC / CRUC) | Unit Water Losses Vol/conn/day | Unit Apparent Losses Vol/conn/day | Unit Real Losses Vol/conn/day | Unit Real Losses per length of main per day | Total Loss Cost Rate $/conn/yr | Apparent Loss Cost Rate $/conn/yr | Real Loss Cost Rate $/conn/yr | Infrastructure Leakage Index (ILI) | Water Audit Data Validity Score | Water Audit Data Validity Tier | Priority Area #1 | Priority Area #2 | Priority Area #3 | Grading: Volume From Own Sources | Grading: Volume From Own Sources MMEA | Grading: Water Imported | Grading: Water Imported MMEA | Grading: Water Exported | Grading: Water Exported MMEA | Grading: Billed Metered | Grading: Billed Unmetered | Grading: Unbilled Metered | Grading: Unbilled Unmetered | Grading: Unauthorized Consumption | Grading: Customer Metering Inaccuracies | Grading: Systematic Data Handling Errors | Grading: Length of Mains | Grading: No. of Active and Inactive Service Connections | Grading: Average length of customer service line | Grading: Average Operating Pressure | Grading: Customer Retail Unit Cost | Grading: Variable Production Cost | vos.0 | vos.1 | vos.2 | vos.3 | vos.4 | vos.5 | vos.6 | vos.7 | vos.8 | vos.9 | vos.10 | vosea.1 | vosea.2 | vosea.3 | vosea.4 | wi.0 | wi.1 | wi.2 | wi.3 | wi.4 | wi.5 | wi.6 | wi.7 | wi.8 | wi.9 | wi.10 | wiea.1 | wiea.2 | wiea.3 | wiea.4 | we.0 | we.1 | we.2 | we.3 | we.4 | we.5 | we.6 | we.7 | we.8 | we.9 | we.10 | weea.1 | weea.2 | weea.3 | weea.4 | bmac.0 | bmac.1 | bmac.2 | bmac.3 | bmac.4 | bmac.5 | bmac.6 | bmac.7 | buac.0 | buac.1 | buac.2 | buac.3 | umac.0 | umac.1 | umac.2 | umac.3 | umac.4 | uuac.0 | uuac.1 | uuac.2 | uuac.3 | sdhe.0 | sdhe.1 | sdhe.2 | sdhe.3 | sdhe.4 | cmi.0 | cmi.1 | cmi.2 | cmi.3 | cmi.4 | cmi.5 | cmi.6 | cmi.7 | cmi.8 | cmi.9 | uc.0 | uc.1 | uc.2 | Lm.1 | Lm.2 | Lm.3 | Lm.4 | Nc.1 | Nc.2 | Nc.3 | Nc.4 | Nc.5 | Lp.0 | Lp.1 | Lp.2 | Lp.3 | Lp.4 | aop.1 | aop.2 | aop.3 | aop.4 | aop.5 | cruc.0 | cruc.1 | cruc.2 | cruc.3 | cruc.4 | vpc.1 | vpc.2 | vpc.3 | vpc.4 | Limiting vos | Limiting vosea | Limiting wi | Limiting wiea | Limiting we | Limiting weea | Limiting bmac | Limiting buac | Limiting umac | Limiting uuac | Limiting sdhe | Limiting cmi | Limiting uc | Limiting Lm | Limiting Nc | Limiting Lp | Limiting aop | Limiting cruc | Limiting vpc | TARGET: Unit Total Losses (vol/conn./day) | TARGET: Unit Apparent Losses (vol/conn./day) | TARGET: Unit Real Losses (vol/conn./day) | TARGET: Unit Real Losses (vol/len./day) | System Input Volume (vol/yr) | Reference Carbon Intensity (g/kWh) | Utility Energy Usage (kWh) | Utility Energy Intensity (kWh/vol) | Utility Carbon Intensity (mt/vol) | System Input Volume (mt/yr) | Current Leakage Level (vol/yr) | Current Leakage Level (mt/yr) | Target Leakage Reduction (vol / yr) | Target Leakage Reduction (mt / yr) | Leakage Level After Reduction (vol / yr) | Leakage Level After Reduction (mt / yr) | Carbon Reduction Calculation Warnings (if any) | General Notes | Notes on Input Derivation (VOS) | Notes on Input Derivation (VOSEA) | Notes on Input Derivation (WI) | Notes on Input Derivation (WIEA) | Notes on Input Derivation (WE) | Notes on Input Derivation (WEEA) | Notes on Input Derivation (BMAC) | Notes on Input Derivation (BUAC) | Notes on Input Derivation (UMAC) | Notes on Input Derivation (UUAC) | Notes on Input Derivation (SDHE) | Notes on Input Derivation (CMI) | Notes on Input Derivation (UC) | Notes on Input Derivation (Lm) | Notes on Input Derivation (Nc) | Notes on Input Derivation (Lp) | Notes on Input Derivation (AOP) | Notes on Input Derivation (CRUC) | Notes on Input Derivation (VPC) | Notes on Input Data Validity Grading (VOS) | Notes on Input Data Validity Grading (VOSEA) | Notes on Input Data Validity Grading (WI) | Notes on Input Data Validity Grading (WIEA) | Notes on Input Data Validity Grading (WE) | Notes on Input Data Validity Grading (WEEA) | Notes on Input Data Validity Grading (BMAC) | Notes on Input Data Validity Grading (BUAC) | Notes on Input Data Validity Grading (UMAC) | Notes on Input Data Validity Grading (UUAC) | Notes on Input Data Validity Grading (SDHE) | Notes on Input Data Validity Grading (CMI) | Notes on Input Data Validity Grading (UC) | Notes on Input Data Validity Grading (Lm) | Notes on Input Data Validity Grading (Nc) | Notes on Input Data Validity Grading (Lp) | Notes on Input Data Validity Grading (AOP) | Notes on Input Data Validity Grading (CRUC) | Notes on Input Data Validity Grading (VPC) | Notes on Reference Carbon Intensity | Notes on Utility Energy Usage | Notes on Target Leakage Reduction | Exchange Rate | FileName | Original Version
2025-11-14 19:49:12.40 UTC | MichaelThompson | -- | -- | Fake Utility | Fakeston | Pennsylvania (PA) | USA | Fake Person | fake@fake.com | 123-456-7890 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45658 | Million gallons (US) | 1234567 | Another Fakeperson | Fakeperson@alsofake.com | 12000 | Retail | Potable Water | 100 | 0 | 10 | 0 | 10 | 0 | 100 | 60 | 10 | 5 | 0.175 | 1 | 75.175 | 24.825 | 0.175 | 1 | 0 |  | 0.175 | 1 | 0.35 | 24.475 | 30 | 50 | 5000 | 100 | No | 25 | 100 | 2000000 | 10 | $/1000 gallons (US) | 500 | 43.7291 | 23.9611 | 0.35 | 24.475 | 5.175 | 30 | 3500 | 12237.5 | 2587.5 | 18325 |  | 13.6027 | 0.19178 | 13.411 | 1341.0959 | 3.1475 | 0.7 | 2.4475 | 0.5597 | 40 | Tier II (26-50) | 1: Volume from Own Sources (VOS) | 2: Billed Metered (BMAC) | 3: Billed Unmetered (BUAC) | 6 |  | 1 |  | 3 |  | 5 | 5 | 2 | 3 | 3 |  | 3 | 1 | 1 | 1 | 3 |  | 1 | Yes | >95 - 99% | At least semi-annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | Between ±3% to ±6% | No | Once per month | Once per month |  |  |  |  | Yes | >90% - 95% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | Not sure | Yes | More frequently than monthly, but not every day | Less frequently than monthly |  |  |  |  | Yes | >50-75% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | At least semi-annually | Yes | At ±6% or greater | Yes | Once per month | Regular review not conducted / Not sure |  |  |  |  | Yes | >10% up to 20% | Bi-Monthly | Yes | Less frequently than annually | Sum total only | Between 3 and 5 years ago | Third party review includes a check on a sample of accounts | Yes | >20% up to 50% | Extrapolated from similar customer groups in the utility's metered population, but limited is sample sizes | Quarterly | Yes | No | Estimated total available | Annually | Less than annually | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | No | [9 empty] | Default is used because Custom Value is selected but no value has been entered |  |  | Guesstimated |  | Mains inventory (GIS, ledger, etc) is not maintained or updated |  | Guesstimated |  |  | Service line inventory (GIS, billing system, etc) is not maintained or updated |  | No | Guesstimated | Additions or subtractions are updated in the service line and meter locations inventory, but less than annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy doesn't exist | Normally-closed boundary valves between zones have never been confirmed to be fully closed | Collected only if there are low pressure complaints, or new development requests | Continuous pressure data is not collected |  | Guesstimated | No |  |  |  |  | Guesstimated | Some but not all applicable short-run marginal costs are included | Long-run marginal costs have not been evaluated for applicability, and are not included | No | vos.9, vos.10 |  | wi.7 |  | we.1, we.10 |  | bmac.1, bmac.4 | buac.2 | umac.1 |  |  |  |  | Lm.1 | Nc.4 | Lp.1, Lp.4 | aop.5 |  | vpc.1 |  |  |  |  | 110 | 474 | 10000000 | 90909.0909 | 43.0909 | 4740 | 24.475 | 1054.65 | 10 | 430.9091 | 14.475 | 623.7409 | Note: Leakage Level After Reduction results in Leakage below the Unavoidable Annual Real Loss volume. | [43 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/FWAS_V6.1 - Copy (2).xlsx | 6.1
2025-11-14 19:49:12.72 UTC | MichaelThompson | -- | -- | Fake Utility | Fakeston | Pennsylvania (PA) | USA | Fake Person | fake@fake.com | 123-456-7890 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45658 | Million gallons (US) | 1234567 | Another Fakeperson | Fakeperson@alsofake.com | 12000 | Retail | Potable Water | 100 | 0 | 10 | 0 | 10 | 0 | 100 | 60 | 10 | 5 | 0.175 | 1 | 75.175 | 24.825 | 0.175 | 1 | 0 |  | 0.175 | 1 | 0.35 | 24.475 | 30 | 50 | 5000 | 100 | No | 25 | 100 | 2000000 | 10 | $/1000 gallons (US) | 500 | 43.7291 | 23.9611 | 0.35 | 24.475 | 5.175 | 30 | 3500 | 12237.5 | 2587.5 | 18325 |  | 13.6027 | 0.19178 | 13.411 | 1341.0959 | 3.1475 | 0.7 | 2.4475 | 0.5597 | 40 | Tier II (26-50) | 1: Volume from Own Sources (VOS) | 2: Billed Metered (BMAC) | 3: Billed Unmetered (BUAC) | 6 |  | 1 |  | 3 |  | 5 | 5 | 2 | 3 | 3 |  | 3 | 1 | 1 | 1 | 3 |  | 1 | Yes | >95 - 99% | At least semi-annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | Between ±3% to ±6% | No | Once per month | Once per month |  |  |  |  | Yes | >90% - 95% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | Not sure | Yes | More frequently than monthly, but not every day | Less frequently than monthly |  |  |  |  | Yes | >50-75% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | At least semi-annually | Yes | At ±6% or greater | Yes | Once per month | Regular review not conducted / Not sure |  |  |  |  | Yes | >10% up to 20% | Bi-Monthly | Yes | Less frequently than annually | Sum total only | Between 3 and 5 years ago | Third party review includes a check on a sample of accounts | Yes | >20% up to 50% | Extrapolated from similar customer groups in the utility's metered population, but limited is sample sizes | Quarterly | Yes | No | Estimated total available | Annually | Less than annually | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | No | [9 empty] | Default is used because Custom Value is selected but no value has been entered |  |  | Guesstimated |  | Mains inventory (GIS, ledger, etc) is not maintained or updated |  | Guesstimated |  |  | Service line inventory (GIS, billing system, etc) is not maintained or updated |  | No | Guesstimated | Additions or subtractions are updated in the service line and meter locations inventory, but less than annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy doesn't exist | Normally-closed boundary valves between zones have never been confirmed to be fully closed | Collected only if there are low pressure complaints, or new development requests | Continuous pressure data is not collected |  | Guesstimated | No |  |  |  |  | Guesstimated | Some but not all applicable short-run marginal costs are included | Long-run marginal costs have not been evaluated for applicability, and are not included | No | vos.9, vos.10 |  | wi.7 |  | we.1, we.10 |  | bmac.1, bmac.4 | buac.2 | umac.1 |  |  |  |  | Lm.1 | Nc.4 | Lp.1, Lp.4 | aop.5 |  | vpc.1 |  |  |  |  | 110 | 474 | 10000000 | 90909.0909 | 43.0909 | 4740 | 24.475 | 1054.65 | 10 | 430.9091 | 14.475 | 623.7409 | Note: Leakage Level After Reduction results in Leakage below the Unavoidable Annual Real Loss volume. | [43 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/FWAS_V6.1 - Copy (3).xlsx | 6.1
2025-11-14 19:49:13.09 UTC | MichaelThompson | -- | -- | Fake Utility | Fakeston | Pennsylvania (PA) | USA | Fake Person | fake@fake.com | 123-456-7890 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45658 | Million gallons (US) | 1234567 | Another Fakeperson | Fakeperson@alsofake.com | 12000 | Retail | Potable Water | 100 | 0 | 10 | 0 | 10 | 0 | 100 | 60 | 10 | 5 | 0.175 | 1 | 75.175 | 24.825 | 0.175 | 1 | 0 |  | 0.175 | 1 | 0.35 | 24.475 | 30 | 50 | 5000 | 100 | No | 25 | 100 | 2000000 | 10 | $/1000 gallons (US) | 500 | 43.7291 | 23.9611 | 0.35 | 24.475 | 5.175 | 30 | 3500 | 12237.5 | 2587.5 | 18325 |  | 13.6027 | 0.19178 | 13.411 | 1341.0959 | 3.1475 | 0.7 | 2.4475 | 0.5597 | 40 | Tier II (26-50) | 1: Volume from Own Sources (VOS) | 2: Billed Metered (BMAC) | 3: Billed Unmetered (BUAC) | 6 |  | 1 |  | 3 |  | 5 | 5 | 2 | 3 | 3 |  | 3 | 1 | 1 | 1 | 3 |  | 1 | Yes | >95 - 99% | At least semi-annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | Between ±3% to ±6% | No | Once per month | Once per month |  |  |  |  | Yes | >90% - 95% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | Not sure | Yes | More frequently than monthly, but not every day | Less frequently than monthly |  |  |  |  | Yes | >50-75% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | At least semi-annually | Yes | At ±6% or greater | Yes | Once per month | Regular review not conducted / Not sure |  |  |  |  | Yes | >10% up to 20% | Bi-Monthly | Yes | Less frequently than annually | Sum total only | Between 3 and 5 years ago | Third party review includes a check on a sample of accounts | Yes | >20% up to 50% | Extrapolated from similar customer groups in the utility's metered population, but limited is sample sizes | Quarterly | Yes | No | Estimated total available | Annually | Less than annually | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | No | [9 empty] | Default is used because Custom Value is selected but no value has been entered |  |  | Guesstimated |  | Mains inventory (GIS, ledger, etc) is not maintained or updated |  | Guesstimated |  |  | Service line inventory (GIS, billing system, etc) is not maintained or updated |  | No | Guesstimated | Additions or subtractions are updated in the service line and meter locations inventory, but less than annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy doesn't exist | Normally-closed boundary valves between zones have never been confirmed to be fully closed | Collected only if there are low pressure complaints, or new development requests | Continuous pressure data is not collected |  | Guesstimated | No |  |  |  |  | Guesstimated | Some but not all applicable short-run marginal costs are included | Long-run marginal costs have not been evaluated for applicability, and are not included | No | vos.9, vos.10 |  | wi.7 |  | we.1, we.10 |  | bmac.1, bmac.4 | buac.2 | umac.1 |  |  |  |  | Lm.1 | Nc.4 | Lp.1, Lp.4 | aop.5 |  | vpc.1 |  |  |  |  | 110 | 474 | 10000000 | 90909.0909 | 43.0909 | 4740 | 24.475 | 1054.65 | 10 | 430.9091 | 14.475 | 623.7409 | Note: Leakage Level After Reduction results in Leakage below the Unavoidable Annual Real Loss volume. | [43 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/FWAS_V6.1 - Copy (4).xlsx | 6.1
2025-11-14 19:49:13.42 UTC | MichaelThompson | -- | -- | Fake Utility | Fakeston | Pennsylvania (PA) | USA | Fake Person | fake@fake.com | 123-456-7890 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45658 | Million gallons (US) | 1234567 | Another Fakeperson | Fakeperson@alsofake.com | 12000 | Retail | Potable Water | 100 | 0 | 10 | 0 | 10 | 0 | 100 | 60 | 10 | 5 | 0.175 | 1 | 75.175 | 24.825 | 0.175 | 1 | 0 |  | 0.175 | 1 | 0.35 | 24.475 | 30 | 50 | 5000 | 100 | No | 25 | 100 | 2000000 | 10 | $/1000 gallons (US) | 500 | 43.7291 | 23.9611 | 0.35 | 24.475 | 5.175 | 30 | 3500 | 12237.5 | 2587.5 | 18325 |  | 13.6027 | 0.19178 | 13.411 | 1341.0959 | 3.1475 | 0.7 | 2.4475 | 0.5597 | 40 | Tier II (26-50) | 1: Volume from Own Sources (VOS) | 2: Billed Metered (BMAC) | 3: Billed Unmetered (BUAC) | 6 |  | 1 |  | 3 |  | 5 | 5 | 2 | 3 | 3 |  | 3 | 1 | 1 | 1 | 3 |  | 1 | Yes | >95 - 99% | At least semi-annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | Between ±3% to ±6% | No | Once per month | Once per month |  |  |  |  | Yes | >90% - 95% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | Not sure | Yes | More frequently than monthly, but not every day | Less frequently than monthly |  |  |  |  | Yes | >50-75% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | At least semi-annually | Yes | At ±6% or greater | Yes | Once per month | Regular review not conducted / Not sure |  |  |  |  | Yes | >10% up to 20% | Bi-Monthly | Yes | Less frequently than annually | Sum total only | Between 3 and 5 years ago | Third party review includes a check on a sample of accounts | Yes | >20% up to 50% | Extrapolated from similar customer groups in the utility's metered population, but limited is sample sizes | Quarterly | Yes | No | Estimated total available | Annually | Less than annually | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | No | [9 empty] | Default is used because Custom Value is selected but no value has been entered |  |  | Guesstimated |  | Mains inventory (GIS, ledger, etc) is not maintained or updated |  | Guesstimated |  |  | Service line inventory (GIS, billing system, etc) is not maintained or updated |  | No | Guesstimated | Additions or subtractions are updated in the service line and meter locations inventory, but less than annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy doesn't exist | Normally-closed boundary valves between zones have never been confirmed to be fully closed | Collected only if there are low pressure complaints, or new development requests | Continuous pressure data is not collected |  | Guesstimated | No |  |  |  |  | Guesstimated | Some but not all applicable short-run marginal costs are included | Long-run marginal costs have not been evaluated for applicability, and are not included | No | vos.9, vos.10 |  | wi.7 |  | we.1, we.10 |  | bmac.1, bmac.4 | buac.2 | umac.1 |  |  |  |  | Lm.1 | Nc.4 | Lp.1, Lp.4 | aop.5 |  | vpc.1 |  |  |  |  | 110 | 474 | 10000000 | 90909.0909 | 43.0909 | 4740 | 24.475 | 1054.65 | 10 | 430.9091 | 14.475 | 623.7409 | Note: Leakage Level After Reduction results in Leakage below the Unavoidable Annual Real Loss volume. | [43 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/FWAS_V6.1 - Copy.xlsx | 6.1
2025-11-14 19:49:13.76 UTC | MichaelThompson | -- | -- | Fake Utility | Fakeston | Pennsylvania (PA) | USA | Fake Person | fake@fake.com | 123-456-7890 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45658 | Million gallons (US) | 1234567 | Another Fakeperson | Fakeperson@alsofake.com | 12000 | Retail | Potable Water | 100 | 0 | 10 | 0 | 10 | 0 | 100 | 60 | 10 | 5 | 0.175 | 1 | 75.175 | 24.825 | 0.175 | 1 | 0 |  | 0.175 | 1 | 0.35 | 24.475 | 30 | 50 | 5000 | 100 | No | 25 | 100 | 2000000 | 10 | $/1000 gallons (US) | 500 | 43.7291 | 23.9611 | 0.35 | 24.475 | 5.175 | 30 | 3500 | 12237.5 | 2587.5 | 18325 |  | 13.6027 | 0.19178 | 13.411 | 1341.0959 | 3.1475 | 0.7 | 2.4475 | 0.5597 | 40 | Tier II (26-50) | 1: Volume from Own Sources (VOS) | 2: Billed Metered (BMAC) | 3: Billed Unmetered (BUAC) | 6 |  | 1 |  | 3 |  | 5 | 5 | 2 | 3 | 3 |  | 3 | 1 | 1 | 1 | 3 |  | 1 | Yes | >95 - 99% | At least semi-annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | Between ±3% to ±6% | No | Once per month | Once per month |  |  |  |  | Yes | >90% - 95% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | Not sure | Yes | More frequently than monthly, but not every day | Less frequently than monthly |  |  |  |  | Yes | >50-75% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | At least semi-annually | Yes | At ±6% or greater | Yes | Once per month | Regular review not conducted / Not sure |  |  |  |  | Yes | >10% up to 20% | Bi-Monthly | Yes | Less frequently than annually | Sum total only | Between 3 and 5 years ago | Third party review includes a check on a sample of accounts | Yes | >20% up to 50% | Extrapolated from similar customer groups in the utility's metered population, but limited is sample sizes | Quarterly | Yes | No | Estimated total available | Annually | Less than annually | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | No | [9 empty] | Default is used because Custom Value is selected but no value has been entered |  |  | Guesstimated |  | Mains inventory (GIS, ledger, etc) is not maintained or updated |  | Guesstimated |  |  | Service line inventory (GIS, billing system, etc) is not maintained or updated |  | No | Guesstimated | Additions or subtractions are updated in the service line and meter locations inventory, but less than annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy doesn't exist | Normally-closed boundary valves between zones have never been confirmed to be fully closed | Collected only if there are low pressure complaints, or new development requests | Continuous pressure data is not collected |  | Guesstimated | No |  |  |  |  | Guesstimated | Some but not all applicable short-run marginal costs are included | Long-run marginal costs have not been evaluated for applicability, and are not included | No | vos.9, vos.10 |  | wi.7 |  | we.1, we.10 |  | bmac.1, bmac.4 | buac.2 | umac.1 |  |  |  |  | Lm.1 | Nc.4 | Lp.1, Lp.4 | aop.5 |  | vpc.1 |  |  |  |  | 110 | 474 | 10000000 | 90909.0909 | 43.0909 | 4740 | 24.475 | 1054.65 | 10 | 430.9091 | 14.475 | 623.7409 | Note: Leakage Level After Reduction results in Leakage below the Unavoidable Annual Real Loss volume. | [43 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/FWAS_V6.1.xlsx | 6.1
2025-11-14 19:49:14.03 UTC | MichaelThompson | -- | -- | Municipal Services Commission | New Castle | Delaware (DE) | United States of America | Jay Guyer - Water Utility Manager | guyerlj@newcastlemsc.delaware.gov | 302-221-4515 | 2024 | Calendar | 12/13/23 - 12/12/24 | 45706 | Million gallons (US) | DE0000634 | N/A | N/A | 5551 | Other ---------------> | Potable Water | 175.837 | 0 | 6.69 | 0 | 24.235 | 0 | 158.292 | 155.115 | 0.325 | 0.519 | 1.643 | 2 | 157.602 | 0.69 | 0.01 | 2 | 0.015565 | 0.0001 | 0.005 | 2 | 0.030565 | 0.65944 | 2.852 | 29 | 2358 | 81.3103 | No | 20 | 50 | 1004435 | 15.72 | $/1000 gallons (US) | 987.85 | 10.5408 | 12.2472 | 0.030565 | 0.65944 | 2.162 | 2.852 | 479.7164 | 651.4229 | 2135.7317 | 3266.871 | VPC | 0.8017 | 0.035513 | 0.76619 | 62.299 | 0.4797 | 0.20344 | 0.27626 | 0.06256 | 82 | Tier IV (71-90) | 1: Volume from Own Sources (VOS) | 2: Customer Metering Inaccuracies (CMI) | 3: Water Exported (WE) | 7 | 9 | 3 | 4 | 7 | 4 | 10 | 10 | 10 | 10 | 8 | 3 | 10 | 10 | 10 | 7 | 7 | 10 | 9 | Yes | >99% | None, or Not within last 5 years |  |  | At least semi-annually | Yes | At or within ±3% | No | Continuous | Daily | Yes | Yes | No | No error adjustment made due to absence of testing or calibration results | Yes | >99% | None, or Not within last 5 years |  |  | None, or Not within last 5 years |  |  |  | Continuous | Once per month | Yes, written | No, but meter accuracy testing and/or electronic calibration is conducted upon request of the importing utility | No | Exporting and Importing Utility | Yes | >99% | None, or Not within last 5 years |  |  | At least semi-annually | Yes | At or within ±3% | No | Continuous | Daily | Yes, written | No, but meter accuracy testing and/or electronic calibration is conducted upon request of the importing utility | No | Exporting and Importing Utility | Yes | 5% or less | More frequently than monthly | Yes | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | Within last 3 years | Full billing database query and analysis of raw data to verify the summary consumption volumes | Yes | 5% or less | Estimated for each unmetered customer OR derived from representative statistical samples of the system | Monthly | Yes | Policy includes specific exemptions | Monitored, count available | Monthly or more frequently | Each billing cycle | A system specific volume has been entered | Complete inventory exists | Each event is documented | Entirely from event-specific estimates | A system specific volume has been entered | Estimation derived from a specific analysis at the account level to identify erroneous unbilled consumption | All meter multipliers have been analyzed to confirm multiplier conversion in the billing system is correct | Policy is clear, and adherance in practice is consistent | Detailed analysis conducted within 3 years of the audit period on stuck meters, extended estimations, & miscoded multipliers | Yes | Reactive testing conducted | No testing conducted, but at least 10% of meter stock has been replaced within two years of the audit period |  | No proactive large meter testing activity to date |  | Calculated based on most recent meter accuracy tests, but not comprehensive of all meter performance | Yes | Replacement upon complete failure or special circumstance (as needed) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | A system specific volume has been entered | Estimation for custom volume derived from system-wide study | Limited investigation performed and documented for unauthorized consumption, beyond reactively discovered events | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | No | Input extrapolated from study sampling a portion of the system | Additions or subtractions are updated in the service line and meter locations inventory, at least annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, and adherance in practice is consistent | Not applicable, the system operates as a single pressure zone | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions, plus some locations inside the zone(s) but not representing the full pressure profile | Year-round data collection via permanent monitoring | Calculated from field data as a simple average | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | Rate structure has only a single volumetric rate, and this was used as the input | No | Yes | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and some but not all applicable costs are included | Yes | vos.2 | vosea.3 | wi.2, wi.5 | wiea.3 | we.2 | weea.3 | [5 empty] | cmi.4 | uc.2 |  |  | Lp.1 | aop.5 |  | vpc.3 | [17 empty] | DRBC Docket Number D-1978-071-CP-3. Data for this report is from December 13, 2023 through December 12, 2024 to match our Monthly Meter Reading dates. | MSC utilizes Badger Magnetic Flow Meters on each water source and a master Magnetic Flow Meter for all combined sources. |  | Water Imported reported is from 3 interconnections, Boothhurst Subdivision, Riveredge Industrial Park, and School Lane Treatment Facility. |  | MSC Exported / Sold finished water to Artesian Water Company through the School Lane Interconnerction during the months of June, July, August, September, and October 2024. |  | See MSC Water Consumption Summary | Riverbend Subdivision Flushing - Twice per Month - See Water Loss Report. Water flushed is billed to the developer until the loop is compled on the dead end main. | City & Free Services - MSC provides free water service to several City Agency Facilities (City Admin, Public Works, Police Station). | See MSC Water Loss Report. |  |  |  | Then length of water mains was takein from the MSC ESRI ArcGIS Pro Mapping System. The distribution System is comprised of 16" Mains, 12" Mains, 8" Mains, 6" Mains, and 4" Mains. Water Services are typically 3/4", 1", 1 1/2", or 2". | The number of service connections was taken from the Monthly Consumption Summary Report maintained by the Administrative Office Billing Department. | Estimated from surveying our distribution system which consists of historc homes with narrow 10ft wide sidewalks to single family homes with minimum 25ft set backs from the property lines to commercial buildings with 100ft plus service lines. Approximately 95% of our residential meters are installed in basements and 5% have meter pits at the property lines. |  | Information is taken from the DRBC Reporting Worksheet prepared by the Administrative Office Billing Department annually. | Information is taken from the DRBC Reporting Worksheet prepared by the Administrative Office Billing Department annually. | After consulting with the meter manufacturer, there is no means to test the accuracy of the mag meters other then to utilize a vessel of a known volume and perfrom a flow test or to use a clamp on untrasonic meter to flow test the Magnetic Flow meters. | [22 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_DE_City of New Castle_1978-071.xlsx | 6.0
2025-11-14 19:49:14.31 UTC | MichaelThompson | -- | -- | TOWN OF MIDDLETOWN | TOWN OF MIDDLETOWN | Delaware (DE) | US | EDWARD MCNATT | EMCNATT@MIDDLETOWN.DELAWARE.GOV | 302-275-0437 | 2024 | CALENDAR YEAR | 01/01/24 - 12/31/24 | 45741 | Million gallons (US) | DE0000614 | EDWARD MCNATT | EMCNATT@MIDDLETOWN.DELAWARE.GOV | 24698 | Hybrid Wholesale + Retail | Potable Water | 301.211 | -0.75491 | 515.263 | -1.2914 | 16.119 | -0.16282 | 802.2385 | 758.411 | 1 | 20.733 | 1.8985 | 1 | 782.0425 | 20.196 | 1.8985 | 1 | 3 | 0.005 | 1.8985 | 1 | 6.7971 | 13.3989 | 42.8275 | 68 | 7353 | 108.1324 | Yes |  | 63 | 4033901 | 3.92 | $/1000 gallons (US) | 5028.31 | 33.8217 | 12.602 | 6.7971 | 13.3989 | 22.6315 | 42.8275 | 26732.9319 | 67373.8232 | 113798.336 | 207905.0911 | VPC | 7.525 | 2.5326 | 4.9924 | 539.8429 | 12.7984 | 3.6356 | 9.1628 | 0.39616 | 37 | Tier II (26-50) | 1: Water Imported (WI) | 2: Billed Metered (BMAC) | 3: Billed Unmetered (BUAC) | 4 | 8 | 3 | 9 | 3 | 4 | 1 | 2 | 10 | 3 | 3 | 3 | 3 | 6 | 5 | 10 | 6 | 7 | 9 | Yes | >90% - 95% | Annually | Data transfer errors are not checked, or not sure | Yes | None, or Not within last 5 years | No |  | No | Daily | Once per month | Yes | Not sure | No | Yes, results are analyzed and incorporated | Yes | >50-75% | None, or Not within last 5 years | [8 empty] | Yes, written | Yes, and stipulated frequency as annual | Yes, results are analyzed and incorporated | Exporting and Importing Utility | Yes | >99% | Less than annual but within last 5 years | Data transfer errors are not checked, or not sure | No | None, or Not within last 5 years |  |  | No | Once per month | Once per month | Yes, written | No, but meter accuracy testing and/or electronic calibration is conducted upon request of the importing utility | No | Exporting and Importing Utility | Yes | 5% or less | Monthly | No | No review |  | More than 5 years ago, or not sure |  | Yes | 5% or less | Estimated based on assumptions of consumption by customer characteristics (i.e. customer type or meter size) | Monthly | Yes | Policy includes specific exemptions | Monitored, count available | Monthly or more frequently | Each billing cycle | Default is used because Custom Value is selected but no value has been entered | Majority identified and tracked | Documentation exists, but not specific to each event | By a mix of some guesstimation and some event-specific estimates | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | Yes | Reactive testing conducted | No proactive small meter testing activity to date |  | Not recurring, but conducted within 5 years prior to audit period | Proactive - all large meters are on a testing schedule | No test results were used, but at least 50% of meter stock has been replaced within two years of the audit period | No | Proactive replacement informed by meter accuracy testing and study of meter performance trends | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), but less than annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Non-premise based, i.e. meter count, customer count | No | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for a portion of the system (i.e. in daily operations or specific validation projects) | Yes |  |  |  |  | Not applicable, the system operates as a single pressure zone | Collected annually during routine system flushing and/or hydrant testing | Continuous pressure data is not collected |  | Calculated from field data as a simple average | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | Rate structure has only a single volumetric rate, and this was used as the input | Yes, but this has not been incorporated into the volume-weighted average calculation | No | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and all applicable costs are included | No | vos.3 | vosea.2 | wi.1 | wiea.2 | we.5 | weea.3 | bmac.4 | buac.2 |  |  |  | cmi.2 |  | Lm.3 | Nc.3 |  | aop.3 | cruc.3 | vpc.4 | [60 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_DE_MIDDLETOWN TOWN_1978-064.xlsx | 6.0
2025-11-14 19:49:14.58 UTC | MichaelThompson | -- | -- | Tidewater Utilities, Inc. |  | Delaware (DE) | United States | Tawanda Priester | tpriester@tuiwater.com | 302-747-1339 | 2024 | Calendar | 01/01/24 - 12/31/24 |  | Million gallons (US) |  |  |  |  | Retail | Potable Water | 302.544 | -4.6073 | 36.3 | 0 | 0 | 0 | 343.4513 | 312.369 | 0 | 0 | 0.78092 | 1 | 313.1499 | 30.3013 | 0.78092 | 1 | 0 |  | 0.78092 | 1 | 1.5618 | 28.7395 | 31.0823 | 84.3 | 4985 | 59.134 | Yes | 7 | 59 |  | 7.88 | $/1000 gallons (US) | 1086.26 | 25.9241 | 14.2477 | 1.5618 | 28.7395 | 0.78092 | 31.0823 | 12307.3386 | 31218.5709 | 848.2849 | 44374.1944 | VPC | 16.6534 | 0.85838 | 15.7951 | 934.0256 | 8.7314 | 2.4689 | 6.2625 | 1.1086 | 63 | Tier III (51-70) | 1: Volume from Own Sources (VOS) | 2: Billed Metered (BMAC) | 3: Variable Production Cost (VPC) | 7 | 8 | 5 | 4 |  |  | 7 |  |  | 3 | 3 | 7 | 3 | 10 | 5 | 10 | 7 | 5 | 4 | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | At or within ±3% | Yes | More frequently than monthly, but not every day | More frequently than monthly, but not every day | Yes | No | No | Yes, results are analyzed and a 'no-adjustment' was determined | Yes | >99% | Less than annual but within last 5 years | Data transfer errors are checked at secondary device(s), but no tertiary device(s) exist | No | Less than annual but within last 5 years | No |  | Yes | Once per month | Once per month | Yes, written | No, but meter accuracy testing and/or electronic calibration is conducted upon request of the importing utility | No | Exporting and Importing Utility | No | [14 empty] | Yes | 5% or less | Quarterly | No | Every billing cycle | Sum total only | Within last 3 years | Third party review includes a check on a sample of accounts | No |  |  |  | No |  |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | Yes | Reactive testing conducted | Ongoing, conducted annually | Testing targeted to subsets of meters ie oldest meters | Ongoing, conducted annually | Proactive - all large meters are on a testing schedule | Calculated based on most recent meter accuracy tests, comprehensive of all meter performance | Yes | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Non-premise based, i.e. meter count, customer count | No | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), but less than annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | Yes |  |  |  |  | Not applicable, the system operates as a single pressure zone | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Year-round data collection via permanent monitoring | Calculated from field data as a simple average | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | Rate structure has multiple volumetric rates, but only one rate was selected for this input | No | Yes | A non-weighted average of multiple sources was calculated | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and some but not all applicable costs are included | Yes | vos.2, vos.3, vos.5 | vosea.2 | wi.2, wi.4, wi.5, wi.6 | wiea.3 |  |  | bmac.2, bmac.5 |  |  |  |  | cmi.3 |  |  | Nc.3 |  | aop.5 | cruc.2 | vpc.1 | [17 empty] | DRBC Docket # D-2005-26 CP-2 | [42 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_DE_Tidewater Utilities Inc. (Garrison Lake - North Dover District)_2005-026.xlsx | 6.0
2025-11-14 19:49:14.85 UTC | MichaelThompson | -- | -- | Tidewater Utilities, Inc. |  | Delaware (DE) | United States | Tawanda Priester | tpriester@tuiwater.com | 302-747-1339 | 2024 | Calendar | 01/01/24 - 12/31/24 |  | Million gallons (US) |  |  |  |  | Other ---------------> | Potable Water | 1391.428 | -21.1893 | 0 | 0 | 0 | 0 | 1412.6173 | 1261.853 | 0 | 0 | 3.1546 | 1 | 1265.0076 | 147.6096 | 3.1546 | 1 | 0 |  | 3.1546 | 1 | 6.3093 | 141.3004 | 150.7643 | 421 | 27139 | 64.4632 | Yes | 7 | 56 |  | 7.88 | $/1000 gallons (US) | 1086.26 | 129.7625 | 13.0997 | 6.3093 | 141.3004 | 3.1546 | 150.7643 | 49717.0082 | 153488.9306 | 3426.7511 | 206632.6899 | VPC | 14.9014 | 0.63693 | 14.2645 | 919.5351 | 7.4876 | 1.8319 | 5.6557 | 1.0889 | 64 | Tier III (51-70) | 1: Volume from Own Sources (VOS) | 2: Billed Metered (BMAC) | 3: Variable Production Cost (VPC) | 7 | 8 |  |  |  |  | 7 |  |  | 3 | 3 | 7 | 3 | 10 | 5 | 10 | 7 | 5 | 4 | vos.0: Yes; vos.1: >99%; vos.2: Annually; vos.3: Data transfer errors are checked at secondary device(s), but not to tertiary device(s); vos.4: Yes; vos.5: Less than annual but within last 5 years; vos.6: Yes; vos.7: At or within ±3%; vos.8: Yes; vos.9: More frequently than monthly, but not every day; vos.10: More frequently than monthly, but not every day; vosea.1: Yes; vosea.2: No; vosea.3: No; vosea.4: Yes, results are analyzed and a 'no-adjustment' was determined; wi.0: No; we.0: No; bmac.0: Yes; bmac.1: 5% or less; bmac.2: Quarterly; bmac.3: No; bmac.4: Every billing cycle; bmac.5: Sum total only; bmac.6: Within last 3 years; bmac.7: Third party review includes a check on a sample of accounts; buac.0: No; umac.0: No; uuac.0: Default is used because Custom Value is selected but no value has been entered; sdhe.0: Default is used because Custom Value is selected but no value has been entered; cmi.0: Yes; cmi.1: Reactive testing conducted; cmi.2: Ongoing, conducted annually; cmi.3: Testing targeted to subsets of meters ie oldest meters; cmi.4: Ongoing, conducted annually; cmi.5: Proactive - all large meters are on a testing schedule; cmi.6: Calculated based on most recent meter accuracy tests, comprehensive of all meter performance; cmi.7: Yes; cmi.8: Annual proactive replacement of subset of meters (i.e. by age or throughput); cmi.9: Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer; uc.0: Default is used because Custom Value is selected but no value has been entered; Lm.1: Derived directly from Mains inventory (GIS, ledger, etc); Lm.2: Yes; Lm.3: Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually; Lm.4: Field validation is accomplished (i.e. in daily operations or specific validation projects); Nc.1: Extracted from Services inventory (GIS, billing system, etc); Nc.2: Non-premise based, i.e. meter count, customer count; Nc.3: No; Nc.4: Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), but less than annually; Nc.5: Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects); Lp.0: Yes; aop.1: Not applicable, the system operates as a single pressure zone; aop.2: Collected annually during routine system flushing and/or hydrant testing; aop.3: At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations); aop.4: Year-round data collection via permanent monitoring; aop.5: Calculated from field data as a simple average; cruc.0: Yes; cruc.1: Customer bill calculations have been checked to confirm the rate structure is correctly implemented; cruc.2: Rate structure has multiple volumetric rates, but only one rate was selected for this input; cruc.3: No; cruc.4: Yes; vpc.1: A non-weighted average of multiple sources was calculated; vpc.2: All applicable short-run marginal costs are included; vpc.3: Long-run marginal costs have been evaluated for applicability, and some but not all applicable costs are included; vpc.4: Yes | vos.2, vos.3, vos.5 | vosea.2 |  |  |  |  | bmac.2, bmac.5 |  |  |  |  | cmi.3 |  |  | Nc.3 |  | aop.5 | cruc.2 | vpc.1 | [17 empty] | DRBC Docket # D-2002-4 CP-2 | [42 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_DE_Tidewater Utilities Inc. (Rehoboth - Lewes)_2002-004.xlsx | 6.0
2025-11-14 19:49:15.11 UTC | MichaelThompson | -- | -- | Town of Milton | Town of Milton | Delaware (DE) | USA | James Kersey | jkersey@ci.milton.de.us | 302-462-1775 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45743 | Million gallons (US) | DE0000629 | James Kersey | jkersey@ci.milton.de.us | 4560 | Retail | Potable Water | 119.1492 | -2.4316 | 0 | 0 | 0 | 0 | 121.5808 | 120.223 | 0 | 0.5933 | 0.30056 | 1 | 121.1169 | 0.46396 | 0.30056 | 1 | 0 |  | 0.30056 | 1 | 0.60111 | -0.13716 | 1.3578 | 23 | 2280 | 99.1304 | Yes |  | 52 |  | 4.35 | $/1000 gallons (US) |  | 8.8528 | 10.6379 | 0.60111 | -0.13716 | 0.89386 | 1.3578 | 2614.8502 | 0 |  | 2614.8502 | VPC | 0.55751 | 0.72232 | -0.16481 | -16.3378 | 1.1469 | 1.1469 | 0 | -0.015493 | 72 | Tier IV (71-90) | 1: Volume from Own Sources (VOS) | 2: Billed Metered (BMAC) | 3: Unauthorized Consumption (UC) | 7 | 9 |  |  |  |  | 7 |  | 8 | 3 | 3 | 6 | 3 | 10 | 10 | 10 | 9 | 9 | 9 | Yes | >95 - 99% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Annually | Yes | At ±6% or greater | Yes | Daily | More frequently than monthly, but not every day | Yes | Yes | No | No error adjustment made due to absence of testing or calibration results | No | [14 empty] | No | [14 empty] | Yes | 5% or less | Quarterly | No | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | Within last 3 years | Third party review includes a check on a sample of accounts | No |  |  |  | Yes | Policy includes specific exemptions | Monitored, count available | Quarterly | Each billing cycle | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | Yes | Reactive testing conducted | No testing conducted, but at least 10% of meter stock has been replaced within two years of the audit period | Testing targeted to subsets of meters ie oldest meters | Not recurring, but conducted within 5 years prior to audit period | Testing targeted to subsets of meters (ie most revenue generating or customer types) | Meter accuracy test results or manufacturer specs are referenced but not analyzed and used directly in calculation | No | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | Yes |  |  |  |  | Not applicable, the system operates as a single pressure zone | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions, plus some locations inside the zone(s) but not representing the full pressure profile | Year-round data collection via permanent monitoring | Derived from hydraulic model, where model has been field calibrated in the last 5 years | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | Rate structure has only a single volumetric rate, and this was used as the input | No | No | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and some but not all applicable costs are included | No | vos.3, vos.7 | vosea.3 |  |  |  |  | bmac.2 |  | umac.3 |  |  | cmi.4, cmi.6 |  |  |  |  | aop.3 | cruc.4 | vpc.3, vpc.4 | [60 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_DE_Town of Milton_1983-022.xlsx | 6.0
2025-11-14 19:49:15.37 UTC | MichaelThompson | -- | -- | City of Camden Water (NJ0408001) | Camden | New Jersey (NJ) | USA | Brian Cianfrani | Brian.Cianfrani@amwater.com | 609-491-6671 | 2024 | Calendar | 01/01/24 - 12/31/24 |  | Million gallons (US) | NJ0408001 | n/a | n/a |  | Retail | Potable Water | 1498.022 | 0 | 934.763 | 0 | 0 | 0 | 2432.785 | 1712 | 38.74 | 36.39 | 79.35 | 2 | 1866.48 | 566.305 | 18.77 | 2 | 162.4187 | 0.085 | 4.3769 | 1 | 185.5656 | 380.7394 | 682.045 | 153 | 14478 | 94.6275 | No | 16 | 45 |  | 5.85 | $/100 cubic feet (ccf) | 1847.44 | 54.6702 | 10.3454 | 185.5656 | 380.7394 | 115.74 | 682.045 | 1430989.6871 | 703393.2098 | 213822.7056 | 2348205.6025 | VPC | 107.164 | 35.1153 | 72.0487 | 6817.7886 | 147.4225 | 98.8389 | 48.5836 | 6.9643 | 77 | Tier IV (71-90) | 1: Billed Unmetered (BUAC) | 2: Billed Metered (BMAC) | 3: Customer Retail Unit Charge (CRUC) | 9 | 8 | 9 | 4 |  |  | 7 | 6 | 8 | 6 | 6 | 7 | 3 | 10 | 10 | 10 | 7 | 5 | 9 | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Daily | Yes | No | No | Yes, results are analyzed and incorporated | Yes | >99% | Not applicable due to no electronic signal output (i.e. to SCADA) |  |  | Annually | No |  | Yes | Daily | Daily | Yes, written | No, but meter accuracy testing and/or electronic calibration is conducted upon request of the importing utility | No | Exporting and Importing Utility | No | [14 empty] | Yes | 5% or less | Quarterly | No | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | Within last 3 years | Third party review includes a check on a sample of accounts | Yes | 5% or less | Estimated for each unmetered customer OR derived from representative statistical samples of the system | Quarterly | Yes | Policy includes specific exemptions | Monitored, count available | Quarterly | Each billing cycle | A system specific volume has been entered | Majority identified and tracked | Documentation exists, but not specific to each event | By number of events multiplied by typical use estimates | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | Yes | Reactive testing conducted | Ongoing, conducted annually | Testing targeted to subsets of meters ie oldest meters | Recurring, within 5 years prior to audit period, but less frequently than annually | Proactive - all large meters are on a testing schedule | Calculated based on most recent meter accuracy tests, but not comprehensive of all meter performance | No | Replacement upon complete failure or special circumstance (as needed) | Records are kept for meter installations, but data is missing for installation date, type, size, or manufacturer | A system specific volume has been entered | Estimation for custom volume extrapolated from study, sampling a portion of the system | All discovered events are recorded | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | No | Derived from full mapping and customer inventory | Additions or subtractions are updated in the service line and meter locations inventory, at least annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, and adherance in practice is consistent | Not applicable, the system operates as a single pressure zone | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Year-round data collection via permanent monitoring | Calculated from field data as a simple average | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | Rate structure has multiple volumetric rates, but only one rate was selected for this input | No | No | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and some but not all applicable costs are included | No | vos.2, vos.5 | vosea.2 | wi.5, wi.9 | wiea.3 |  |  | bmac.2 | buac.3 | umac.3 | uuac.2 |  | cmi.3 | uc.2 |  |  |  | aop.5 | cruc.2 | vpc.3, vpc.4 | [17 empty] | Efforts over last year in the Distribution Division resulted in fourteen (14) main repairs (breaks/leaks). In addition seven (7) service lines were replaced (main to curb), twenty (20) water service lines were repaired (main to curb), and eight (8) abandoned water service lines were terminated at their respective water mains (these abandoned service lines reported as leaks). | The system totally relies on groundwater supply. The individual wells feed one of two (2) treatment plants, each plant has a finished water meter. The WTP effluent meters are being used for this audit. The City's planned meter change out program has been delayed and revised to only include customer meters. Replacement of the production meters have been identified in the City's five (5) year Capital Program, but due to current supply constraints attributed to PFC levels in some of the wells, only the seven (7) active wells had their meters replaced in 2021. An additional seven (7) well meters are scheduled to be replaced in 2025 in preperation of the new PFAS facility being brought on-line later in the year. | The Master meters for both WTP's (Morris-Delair and Parkside) were tested in 2024 (Morris-Delair & Parkside in May), respectively. Morris-Delair's master meter was found to be registering at 99.1% and the Parkside master meter was found to be registering at 100.2%. The accuracy level of the meters after testing fell within the American Water Works Association (AWWA) acceptance limit range of 98 to 102 percent. | The City of Camden's Water system imported 934.763 million gallons of potable water in 2024 through an adjacent interconnect with New Jersey American Water to supplement the systems supply due to wells being taken out of service for elevated PFC levels. | NJAW is responsible for the interconnect flow meter. | None | None | Switched billing providers at the end of 2019, which is resulting in enhanced consumption accuracy, while also providing guidance and support to the focused meter change out program. We continue to investigate and refine the accuracy of billing and reducing the number of estimated bills. | Identified 270 acounts that remain unmetered. Consumption equals 270 x 48ccf x 7.48 x 4 = 38.74 MG/year. The unmetered accounts identified will be metered under the continuing meter change out program. | Twenty-seven (27) municipal facilities (City Hall, Police Station, Fire Stations, DPW facilities and Park Dept. Spray Pools) are metered, but not billed. These meters are being read quarterly. The CIS system indicated 36.39 MG of recorded usage associated with these connections. | Hydrant flushing; hydrant flushed semi-annually- 27.34 MG; Water System Maintenance; Backwash to waste 6.13 MG; Sewer System Maintenance; 144,998 feet of combined sewer mains cleaned and cctv'd- 37.71 MG, which is lower than previous years due to the contractor utilizing multiple water recyclable units; Fire Department use(54 structure fires in 2024, and testing)- 5.77 MG; Dust Control for demolition projects- 2.4 MG | Continuing to address issues associated with number of finaled accounts and vacant properties. | 61% of billed consumption goes through 443 commercial meters and 39% of the billed consumption goes through approximately 13,399 residential meters. Based on the meter accuracy testing of two hundrend and eight (208) commercial meters and nine (9) residential meters, the average meter inaccuracy ranges between 5 and 15%. For this audit, we have selected 8.5% loss for average meter inaccuracy. | 18.77 MG estimated for the combination of illegal use of opening fire hydrants during the summer months, and a combination of water main breaks/leaks. | "As-builts" are required by the City for all projects. Efforts to update the GIS and CMMS systems with "As-built" drawings continues. | Recently discovered number of service connections in our billing system during "LSL Inventory". Continuing to address issues associated with number of demolished structures and vacant properties. | By City Ordinance, the customer is responsible for the installation and maintenance of the water service; the face of the curb delineates the change in "ownership" of the service line. | System consists of a single pressure zone. Pressure is monitored at the three (3) treated water storage tanks via SCADA. | Residential Rates (Tiered System): $4.02/ccf for the first 15 ccf; $6.03/ccf for the next 15 ccf; $7.98/ccf for consumption over 30 ccf. Commercial: $6.03/ccf. Estimated consumption for unmetered accounts/missed reads/zero consumption accounts is 48 ccf/quarter. The City recently passed a rate increase effective 4th quarter 2023 after conducting a rate study the last few years as the last rate increases were implemented in 2013. | Actual spend on chemicals ($ 412,678.97), power ($ 636,511.94) and residuals disposal ($ 97,624.35) for treatment facilities. Bulk water purchase total ($3,347,618.56) | [23 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_NJ_Camden City_1979-083.xlsx | 6.0
2025-11-14 19:49:15.63 UTC | MichaelThompson | -- | -- | Borough of Glassboro | Glassboro | New Jersey (NJ) | USA | Russell Clark Jr. | cclark@glassboro.org | 856-863-3612 | 2024 | 2024 | 01/01/24 - 12/31/24 |  | Million gallons (US) | NJ0806001 |  |  | 20786 |  | Potable Water | 507.849 | -5.1298 | 317.755 | -3.2096 | 119.383 | -2.4364 | 712.124 | 646.802 | 0 | 1.881 | 1.617 | 1 | 650.3 | 61.824 | 1.617 | 1 | 0 |  | 1.617 | 1 | 3.234 | 58.59 | 65.322 | 85 | 6412 | 75.4353 | No | 60 | 52 |  | 6.06 | $/1000 gallons (US) | 1473 | 37.3551 | 15.9611 | 3.234 | 58.59 | 3.498 | 65.322 | 19598.1006 | 86303.1165 | 5152.5614 | 111053.7785 | VPC | 26.4162 | 1.3818 | 25.0344 | 1888.4781 | 16.5161 | 3.0565 | 13.4596 | 1.5685 | 45 | Tier II (26-50) | 1: Volume from Own Sources (VOS) | 2: Water Imported (WI) | 3: Billed Metered (BMAC) | 4 | 10 | 1 | 4 | 1 | 4 | 5 |  | 8 | 3 | 3 | 2 | 3 | 10 | 10 | 10 | 5 | 1 | 9 | Yes | >99% | Less than annual but within last 5 years | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | At or within ±3% | Yes | Less frequently than monthly | Less frequently than monthly | Yes | Yes | Yes | No error adjustment made due to absence of testing or calibration results | Yes | <25% | [9 empty] | Yes, written | Yes, and stipulated as less frequent than annual | No | Exporting Utility only | Yes | <25% | [9 empty] | Yes, written | Yes, and stipulated as less frequent than annual | No | Exporting Utility only | Yes | 5% or less | Quarterly | No | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | Within last 3 years | Not sure | No |  |  |  | Yes | Policy includes specific exemptions | Monitored, count available | Quarterly | Each billing cycle | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | Yes | Reactive testing conducted | No proactive small meter testing activity to date |  | No proactive large meter testing activity to date |  | Guesstimated without any customer meter testing data as a reference | No | Replacement upon complete failure or special circumstance (as needed) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | No | Derived from full mapping and customer inventory | Additions or subtractions are updated in the service line and meter locations inventory, at least annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, and adherance in practice is consistent | Not applicable, the system operates as a single pressure zone | Collected only if there are low pressure complaints, or new development requests | Continuous pressure data is not collected |  | Loose estimate inferred from field measurements, but no analysis nor calculations performed | Yes | Customer bill calculations have not been checked to confirm the rate structure is correctly implemented | A volume-weighted average of all rates was calculated | Yes, but this has not been incorporated into the volume-weighted average calculation | No | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and some but not all applicable costs are included | No | vos.9, vos.10 |  | wi.1 | wiea.3 | we.1 | weea.3 | bmac.7 |  | umac.3 |  |  | cmi.6 |  |  |  |  | aop.5 | cruc.1 | vpc.3, vpc.4 | [60 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_NJ_Glassboro Borough Water Dept_1996-054.xlsx | 6.0
2025-11-14 19:49:15.97 UTC | MichaelThompson | -- | -- | Montague Water and Sewer | Montague | New Jersey (NJ) | USA | Doug Cafaro | Doug.Cafaro@nexuswg.com | 973-459-2664 | 2024 | 2024 | 01/01/24 - 12/31/24 | 45691 | Million gallons (US) | 1914002 | N/A | N/A | 2165 | Retail | Potable Water | 29.625 | 0 |  | 0 |  | 0 | 29.625 | 24.943 |  | 0.252 | 0.144 | 2 | 25.339 | 4.286 | 0.062358 | 1 | 0.012604 | 0.0005 | 0.062358 | 1 | 0.13732 | 4.1487 | 4.682 | 11.75 | 802 | 68.2553 | No | 60 | 80 | 767145.96 | 17.98 | $/1000 gallons (US) | 561.8 | 7.3648 | 25.1591 | 0.13732 | 4.1487 | 0.396 | 4.682 | 2466.7963 | 2330.7291 | 222.4728 | 5019.9982 | VPC | 14.6415 | 0.4691 | 14.1724 | 967.3404 | 5.982 | 3.0758 | 2.9061 | 0.56331 | 71 | Tier IV (71-90) | 1: Volume from Own Sources (VOS) | 2: Customer Metering Inaccuracies (CMI) | 3: Billed Metered (BMAC) | 7 | 4 |  |  |  |  | 7 |  | 4 | 5 | 3 | 3 | 3 | 10 | 10 | 10 | 7 | 10 | 10 | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Daily | Daily | Yes | No | No | Results are available but not analyzed | No | [14 empty] | No | [14 empty] | Yes | 5% or less | Monthly | No | Every billing cycle | Sum total only | More than 5 years ago, or not sure | Not sure | No |  |  |  | Yes | Policy broadly addresses and there exists a collective understanding | Monitored, count available | Monthly or more frequently | Each billing cycle | A system specific volume has been entered | Majority identified and tracked | Each event is documented | By a mix of some guesstimation and some event-specific estimates | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | Yes | Reactive testing conducted | No proactive small meter testing activity to date | Testing targeted to subsets of meters ie oldest meters | Ongoing, conducted annually | Proactive - all large meters are on a testing schedule | Meter accuracy test results or manufacturer specs are referenced but not analyzed and used directly in calculation | Yes | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | No | Derived from full mapping and customer inventory | Additions or subtractions are updated in the service line and meter locations inventory, at least annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, and adherance in practice is consistent | Not applicable, the system operates as a single pressure zone | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Year-round data collection via permanent monitoring | Calculated from field data as a simple average | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | Rate structure has only a single volumetric rate, and this was used as the input | No | Yes | Only one source of water exists, which was the basis for the input derivation | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and all applicable costs are included | Yes | vos.3 | vosea.4 |  |  |  |  | bmac.5 |  | umac.1 | uuac.3 |  | cmi.2 |  |  |  |  | aop.5 | [62 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_NJ_MONTAGUE WATER CO_1991-075.xlsx | 6.0
2025-11-14 19:49:16.29 UTC | MichaelThompson | -- | -- | NJ0327001 - NJAW Delaware | Camden | New Jersey (NJ) | United States | Alex Buyser | alex.buyser@amwater.com | 6102923569 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45742 | Million gallons (US) | NJ0327001 - NJAW Delaware | n/a | n/a | 279898 | Retail | Potable Water | 15842.187 | 0 | 7.833 | 0 | 5930.977 | 0 | 9919.043 | 8603.964 | 0 | 0 | 79.2109 | 2 | 8683.1749 | 1235.8681 | 21.5099 | 1 | 21.5638 | 0.0025 | 12.9059 | 2 | 55.9797 | 1179.8884 | 1315.079 | 1406 | 104695 | 74.463 | No | 25 | 58 | 21269428 | 7.7752 | $/1000 gallons (US) | 545 | 572.1949 | 14.9736 | 55.9797 | 1179.8884 | 79.2109 | 1315.079 | 435253.1733 | 643039.1723 | 43169.9596 | 1121462.3052 | VPC | 32.341 | 1.4649 | 30.8761 | 2299.1258 | 10.2994 | 4.1573 | 6.142 | 2.062 | 76 | Tier IV (71-90) | 1: Customer Metering Inaccuracies (CMI) | 2: Billed Metered (BMAC) | 3: Number of Service Connections (Nc) | 9 | 8 | 9 | 9 | 9 | 9 | 8 |  |  | 10 | 3 | 2 | 5 | 10 | 5 | 1 | 8 | 10 | 10 | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Daily | Yes | No | No | Yes, results are analyzed and a 'no-adjustment' was determined | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Daily | Yes, written | Yes, and stipulated frequency as annual | Yes, results are analyzed and a 'no-adjustment' was determined | Exporting and Importing Utility | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Daily | Yes, written | Yes, and stipulated frequency as annual | Yes, results are analyzed and a 'no-adjustment' was determined | Exporting and Importing Utility | Yes | 5% or less | Monthly | Yes | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | More than 5 years ago, or not sure | Full billing database query and analysis of raw data to verify the summary consumption volumes | No |  |  |  | No |  |  |  |  | A system specific volume has been entered | Complete inventory exists | Each event is documented | Entirely from event-specific estimates | A system specific volume has been entered | Estimation derived from a specific analysis at the account level to identify erroneous unbilled consumption | All meter multipliers have been analyzed to confirm multiplier conversion in the billing system is correct | Policy is clear, but adherance in practice is inconsistent | Detailed analysis conducted within 3 years of the audit period on stuck meters, extended estimations, & miscoded multipliers | Yes | Reactive testing conducted | Recurring, within 5 years prior to audit period | Proactive - representative sample (for small meters) | Recurring, within 5 years prior to audit period, but less frequently than annually | Proactive - all large meters are on a testing schedule | Guesstimated without any customer meter testing data as a reference | No | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, but data is missing for installation date, type, size, or manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | No | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | No | Guesstimated | Additions or subtractions are updated in the service line and meter locations inventory, at least annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, and adherance in practice is consistent | Normally-closed boundary valves between zones have been confirmed within the past 3 years to be fully closed | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Year-round data collection via permanent monitoring | Derived from hydraulic model, where model has been field calibrated in the last 5 years | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | Rate structure has only a single volumetric rate, and this was used as the input | No | Yes | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and all applicable costs are included | Yes | vos.2, vos.5 | vosea.2 | wi.2, wi.5 | wiea.2 | we.2, we.5 | weea.2 | bmac.6 |  |  |  | sdhe.3 | cmi.6 |  |  | Nc.3 | Lp.1 | aop.3 | [19 empty] | D-1990-108 CP-3 | Surface and Ground Water | [5 empty] | All metering in compliance with NJAC and regulated by NJBPU tariff |  |  | Used 0.3% of System Delivery. Full flushing records are kept in Work Management System (Mapcall) | industry estimate is used | NJDEP meter testing requirements. +/- 2% is industry standard | Based on theft of service reporting practice (internal) | from GIS | from CRM and historical data | Estimated | from hydraulic model | per tariff Medford IC | cost by operating center. Not available by PWSID. | [23 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_NJ_NJAW (Delaware)_1990-108.xlsx | 6.0
2025-11-14 19:49:16.56 UTC | MichaelThompson | -- | -- | NJ1011001 - Frenchtown | Camden | New Jersey (NJ) | United States | Alex Buyser | alex.buyser@amwater.com | 6102923569 | 2024 | Calender | 01/01/24 - 12/31/24 | 45742 | Million gallons (US) | NJ1011001 - Frenchtown | n/a | n/a | 1496 | Retail | Potable Water | 33.15 | 0 | 0 | 0 | 0 | 0 | 33.15 | 27.731 | 0 | 0 | 0.43095 | 2 | 28.162 | 4.9881 | 0.069328 | 1 | 0.069501 | 0.0025 | 0.069328 | 1 | 0.20816 | 4.7799 | 5.419 | 8 | 512 | 64 | No | 25 | 73 | 495785 | 7.77 | $/1000 gallons (US) | 886 | 3.684 | 19.7131 | 0.20816 | 4.7799 | 0.43095 | 5.419 | 1617.3741 | 4234.9859 | 381.8217 | 6234.1816 | VPC | 26.6912 | 1.1138 | 25.5773 | 1636.9499 | 11.4304 | 3.1589 | 8.2715 | 1.2975 | 77 | Tier IV (71-90) | 1: Customer Metering Inaccuracies (CMI) | 2: Volume from Own Sources (VOS) | 3: Number of Service Connections (Nc) | 9 | 8 | 9 | 9 |  |  | 9 |  |  | 10 | 3 | 2 | 3 | 10 | 5 | 1 | 8 | 10 | 10 | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Daily | Yes | No | No | Yes, results are analyzed and a 'no-adjustment' was determined | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Daily | Yes, written | Yes, and stipulated frequency as annual | Yes, results are analyzed and a 'no-adjustment' was determined | Exporting and Importing Utility | No | [14 empty] | Yes | 5% or less | Monthly | Yes | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | Within last 3 years | Full billing database query and analysis of raw data to verify the summary consumption volumes | No |  |  |  | No |  |  |  |  | A system specific volume has been entered | Complete inventory exists | Each event is documented | Entirely from event-specific estimates | Default is used because Custom Value is selected but no value has been entered | Estimation derived from a specific analysis at the account level to identify erroneous unbilled consumption | All meter multipliers have been analyzed to confirm multiplier conversion in the billing system is correct | Policy is clear, but adherance in practice is inconsistent | Detailed analysis conducted within 3 years of the audit period on stuck meters, extended estimations, & miscoded multipliers | Yes | Reactive testing conducted | Recurring, within 5 years prior to audit period | Proactive - representative sample (for small meters) | Recurring, within 5 years prior to audit period, but less frequently than annually | Proactive - all large meters are on a testing schedule | Guesstimated without any customer meter testing data as a reference | No | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | No | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | No | Guesstimated | Additions or subtractions are updated in the service line and meter locations inventory, at least annually | No field validation is conducted | Policy is clear, and adherance in practice is consistent | Normally-closed boundary valves between zones have been confirmed within the past 3 years to be fully closed | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Year-round data collection via permanent monitoring | Derived from hydraulic model, where model has been field calibrated in the last 5 years | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | A volume-weighted average of all rates was calculated | No | Yes | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and all applicable costs are included | Yes | vos.2, vos.5 | vosea.2 | wi.2, wi.5 | wiea.2 |  |  | bmac.2 |  |  |  |  | cmi.6 |  |  | Nc.3 | Lp.1 | aop.3 | [19 empty] | D-1968-115 CP | Ground Water | annual Check |  | n/a | n/a |  | All metering in compliance with NJAC and regulated by NJBPU tariff |  |  | Used 0.3% of System Delivery. Full flushing records are kept in Work Management System (Mapcall) | industry estimate is utilized | NJDEP meter testing requirements. +/- 2% is industry standard | Based on theft of service reporting practice (internal) | From GIS | from CRM and historical data | Customers are all commercial, meters are set in hot boxes near the property lines | From Hydraulic Model | as established by tariff | cost by operating center. Not available by PWSID. | [23 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_NJ_NJAW (Frenchtown)_1968-115.xlsx | 6.0
2025-11-14 19:49:16.84 UTC | MichaelThompson | -- | -- | NJ0808001 - NJAW Harrison | Camden | New Jersey (NJ) | United States | Alex Buyser | alex.buyser@amwater.com | 6102923569 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45742 | Million gallons (US) | NJ0808001 - NJAW Harrison | n/a | n/a | 8210 | Retail | Potable Water | 119.761 | 0 | 266.883 | 0 | 0 | 0 | 386.644 | 372.777 | 0 | 0 | 1.7964 | 2 | 374.5734 | 12.0706 | 0.93194 | 1 | 0.93428 | 0.0025 | 0.037278 | 2 | 1.9035 | 10.1671 | 13.867 | 71 | 3327 | 46.8592 | No | 25 | 52 | 1074296 | 7.78 | $/1000 gallons (US) | 545 | 19.0048 | 15.6501 | 1.9035 | 10.1671 | 1.7964 | 13.867 | 14809.2175 | 5541.0622 | 979.0462 | 21329.3259 | VPC | 9.9399 | 1.5675 | 8.3724 | 392.3244 | 6.1167 | 4.4512 | 1.6655 | 0.53497 | 76 | Tier IV (71-90) | 1: Customer Metering Inaccuracies (CMI) | 2: Billed Metered (BMAC) | 3: Number of Service Connections (Nc) | 9 | 8 | 9 | 9 |  |  | 8 |  |  | 10 | 3 | 2 | 5 | 10 | 5 | 1 | 8 | 10 | 10 | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Daily | Yes | No | No | Yes, results are analyzed and a 'no-adjustment' was determined | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Daily | Yes, written | Yes, and stipulated frequency as annual | Yes, results are analyzed and a 'no-adjustment' was determined | Exporting and Importing Utility | No | [14 empty] | Yes | 5% or less | Monthly | Yes | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | More than 5 years ago, or not sure |  | No |  |  |  | No |  |  |  |  | A system specific volume has been entered | Complete inventory exists | Each event is documented | Entirely from event-specific estimates | A system specific volume has been entered | Estimation derived from a specific analysis at the account level to identify erroneous unbilled consumption | All meter multipliers have been analyzed to confirm multiplier conversion in the billing system is correct | Policy is clear, but adherance in practice is inconsistent | Detailed analysis conducted within 3 years of the audit period on stuck meters, extended estimations, & miscoded multipliers | Yes | Reactive testing conducted | Recurring, within 5 years prior to audit period | Proactive - representative sample (for small meters) | Recurring, within 5 years prior to audit period, but less frequently than annually | Proactive - all large meters are on a testing schedule | Guesstimated without any customer meter testing data as a reference | No | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, but data is missing for installation date, type, size, or manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | No | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | No | Guesstimated | Additions or subtractions are updated in the service line and meter locations inventory, at least annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, and adherance in practice is consistent | Normally-closed boundary valves between zones have been confirmed within the past 3 years to be fully closed | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Year-round data collection via permanent monitoring | Derived from hydraulic model, where model has been field calibrated in the last 5 years | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | Rate structure has only a single volumetric rate, and this was used as the input | No | Yes | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and all applicable costs are included | Yes | vos.2, vos.5 | vosea.2 | wi.2, wi.5 | wiea.2 |  |  | bmac.6 |  |  |  | sdhe.3 | cmi.6 |  |  | Nc.3 | Lp.1 | aop.3 | [19 empty] | Docket D-99-057 CP-1. This one of numerous contiguous water systems owned and operated by New Jersey American Water. The sources of supply are Woodland and Mill Road Stations. Water supply is supplemented with water sources from the Delaware system. Interconnection at Tomlin Station and Helig Roads. System also includes Walnut Glen ASR. | Combined ground water and surface/ground water (import from Delaware) | Annual Check |  |  |  |  | All metering in compliance with NJAC and regulated by NJBPU tariff |  |  | Used 0.3% of System Delivery. Full flushing records are kept in Work Management System (Mapcall) | industry estimate is used | NJDEP meter testing requirements. +/- 2% is industry standard | Based on theft of service reporting practice (internal) | from gIS | from CRM and historical data | Estimated | from hydraulic model | per tariff Medford IC | cost by operating center. Not available by PWSID. | [6 empty] | Harrison System is adjacent to the larger NJAW Delaware PWSID. Individual premise locations can be placed in the wrong PWSID and continuous data validation is needed. 2023 Inspira Medical Center was assigned to this PWSID and not the Delaware making consumption greater than System Delivery. | [16 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_NJ_NJAW (Harrison)_1999-057.xlsx | 6.0
2025-11-14 19:49:17.10 UTC | MichaelThompson | -- | -- | Village of Deposit | Village of Deposit | New York (NY) | United States | Steve Evans | VOD.Supervisor.Evans@gmail.com | 607-467-2492 | 2024 | Fiscal | 01/01/24 - 12/31/24 | 45754 | Million gallons (US) | 0301663 | n/a | n/a | 2811 | Retail | Potable Water | 111.298 | -12.3664 | 0 | 0 | 0.396 | 0 | 123.2684 | 50.78 | 0 | 7.744 | 0.12695 | 1 | 58.651 | 64.6175 | 0.12695 | 1 | 3.0802 | 0.05 | 0.12695 | 1 | 3.3341 | 61.2834 | 72.4884 | 12.7 | 683 | 53.7795 | No | 50 | 60 |  | 7.75 | $/1000 gallons (US) | 557.45 | 4.8107 | 19.2971 | 3.3341 | 61.2834 | 7.8709 | 72.4884 | 22907.8246 | 34162.4224 | 4387.6611 | 61457.9081 | VPC | 259.2009 | 13.3742 | 245.8268 | 13220.4474 | 83.5582 | 33.54 | 50.0182 | 12.739 | 46 | Tier II (26-50) | 1: Volume from Own Sources (VOS) | 2: Customer Metering Inaccuracies (CMI) | 3: Billed Metered (BMAC) | 1 | 8 |  |  | 3 | 4 | 7 |  | 5 | 3 | 3 | 2 | 3 | 10 | 10 | 10 | 7 | 9 | 4 | Yes | >99% | None, or Not within last 5 years |  |  | None, or Not within last 5 years |  |  |  | Less frequently than monthly | Regular review not conducted / Not sure | Yes | No | No | No error adjustment made due to absence of testing or calibration results | No | [14 empty] | Yes | >99% | None, or Not within last 5 years |  |  | None, or Not within last 5 years |  |  |  | Daily | More frequently than monthly, but not every day | Yes, written | Yes, and stipulated as more frequent than annual | No | Exporting Utility only | Yes | 5% or less | Quarterly | No | Annually | Sum total only | More than 5 years ago, or not sure |  | No |  |  |  | Yes | Policy includes specific exemptions | Monitored, count available | Quarterly | Less than annually | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | Yes | Reactive testing conducted | No testing conducted, but at least 10% of meter stock has been replaced within two years of the audit period |  | Not recurring, but conducted within 5 years prior to audit period | Testing targeted to subsets of meters (ie most revenue generating or customer types) | Guesstimated without any customer meter testing data as a reference | No | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | No | Derived from full mapping and customer inventory | Additions or subtractions are updated in the service line and meter locations inventory, at least annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, and adherance in practice is consistent | Not applicable, the system operates as a single pressure zone | Collected only if there are low pressure complaints, or new development requests | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Temporary data logger(s) deployed, but limited and not capturing seasonal variation during the year | Derived from hydraulic model, where model has been field calibrated in the last 5 years | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | Rate structure has only a single volumetric rate, and this was used as the input | No | No | A non-weighted average of multiple sources was calculated | All applicable short-run marginal costs are included | Long-run marginal costs have not been evaluated for applicability, and are not included | No | vos.10 | vosea.2 |  |  | we.2, we.5 | weea.3 | bmac.2, bmac.5 |  | umac.4 |  |  | cmi.6 |  |  |  |  | aop.4 | cruc.4 | vpc.1 | [60 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_NY_Deposit Village_1999-064.xlsx | 6.0
2025-11-14 19:49:17.41 UTC | MichaelThompson | -- | -- | Village of Fleischmanns | Fleischwwtp@gmail.com | New York (NY) | United States | Todd Murphy | Fleischwwtp@gmail.com | 845-254-5945 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45731 | Million gallons (US) | NY1200261 | N/A |  |  | Retail | Potable Water | 31.8 | 0 | 0 | 0 | 0 | 0 | 31.8 | 16.3 | 0 | 0 | 0.04075 | 1 | 16.3407 | 15.4593 | 0.04075 | 1 | 0 |  | 0.04075 | 1 | 0.0815 | 15.3778 | 15.5 | 3.7 | 248 | 67.027 | No | 100 | 70 |  | 16 | $/100 cubic feet (ccf) |  | 2.362 | 26.0931 | 0.0815 | 15.3778 | 0.04075 | 15.5 | 1743.1945 | 0 |  | 1743.1945 | VPC | 170.7827 | 0.90035 | 169.8823 | 11386.7086 | 7.029 | 7.029 | 0 | 6.5106 | 37 | Tier II (26-50) | 1: Volume from Own Sources (VOS) | 2: Customer Metering Inaccuracies (CMI) | 3: Billed Metered (BMAC) | 1 | 8 |  |  |  |  | 7 |  |  | 3 | 3 | 2 | 3 | 6 | 5 | 1 | 7 | 5 | 8 | vos.0: Yes; vos.1: >99%; vos.2: None, or Not within last 5 years; vos.5: None, or Not within last 5 years; vos.9: Daily; vos.10: Regular review not conducted / Not sure; vosea.1: Yes; vosea.2: No; vosea.3: Yes; vosea.4: No error adjustment made due to absence of testing or calibration results; wi.0: No; we.0: No; bmac.0: Yes; bmac.1: >5% up to 10%; bmac.2: Quarterly; bmac.3: No; bmac.4: Every billing cycle; bmac.5: Sum total only; bmac.6: More than 5 years ago, or not sure; buac.0: No; umac.0: No; uuac.0: Default is used because Custom Value is selected but no value has been entered; sdhe.0: Default is used because Custom Value is selected but no value has been entered; cmi.0: Yes; cmi.1: Reactive testing conducted; cmi.2: No proactive small meter testing activity to date; cmi.4: No proactive large meter testing activity to date; cmi.6: Guesstimated without any customer meter testing data as a reference; cmi.7: No; cmi.8: Replacement upon complete failure or special circumstance (as needed); cmi.9: Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer; uc.0: Default is used because Custom Value is selected but no value has been entered; Lm.1: Derived directly from Mains inventory (GIS, ledger, etc); Lm.2: No; Lm.3: Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), but less than annually; Lm.4: No field validation is conducted; Nc.1: Extracted from Services inventory (GIS, billing system, etc); Nc.2: Non-premise based, i.e. meter count, customer count; Nc.3: Yes; Nc.4: Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually; Nc.5: No field validation is conducted; Lp.0: No; Lp.1: Input extrapolated from study sampling a portion of the system; Lp.2: Customer Service Line and Meter Locations inventory is not maintained or updated; Lp.4: Policy is clear, and adherance in practice is consistent; aop.1: Not applicable, the system operates as a single pressure zone; aop.2: Collected annually during routine system flushing and/or hydrant testing; aop.3: At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations); aop.4: Temporary data logger(s) deployed, adequately capturing seasonal variation during the year; aop.5: Calculated from field data as a simple average; cruc.0: Yes; cruc.1: Customer bill calculations have been checked to confirm the rate structure is correctly implemented; cruc.2: Rate structure has multiple volumetric rates, but only one rate was selected for this input; cruc.3: Yes, and this has been incorporated into the volume-weighted average calculation; cruc.4: No; vpc.1: Only one source of water exists, which was the basis for the input derivation; vpc.2: All applicable short-run marginal costs are included; vpc.3: Long-run marginal costs have not been evaluated for applicability, and are not included; vpc.4: No | vos.10 | vosea.2 |  |  |  |  | bmac.1, bmac.2, bmac.5 |  |  |  |  | cmi.6 |  | Lm.3 | Nc.5 | Lp.2 | aop.5 | cruc.2 | vpc.3 | [60 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_NY_Fleischmanns Village_2009-008.xlsx | 6.0
2025-11-14 19:49:17.68 UTC | MichaelThompson | TRUE | TRUE | village of margaretville water | village of margaretville water | New York (NY) | delawre | johnpaul beers | vom dpw @ catskill.net | 8455863700 | 2024 | 2024 | 01/01/24 - 12/31/25 | 45727 | Million gallons (US) | 1200268 | n/a | vomdpw2catskill.net | 600 | Retail | Potable Water | 45.8 | 0 |  | 0 |  | 0 | 45.8 | 17000 |  |  | 42.5 | 1 | 17042.5 | -16996.7 | 42.5 | 1 | 0 |  | 42.5 | 1 | 85 | -17081.7 | -16954.2 | 8.5 | 300 | 35.2941 | No | 35 | 70 |  | 6.25 | $/1000 gallons (US) | 165 | 2.7057 | 24.7099 | 85 | -17081.7 | 42.5 | -16954.2 | 531250 | -2818480.5 |  | -2287230.5 | VPC | [9 empty] | TBD |  |  |  | 7 | 9 |  |  |  |  | 7 |  |  | 3 | 3 | 6 | 3 | 10 | 8 | 6 | 6 | 9 |  | vos.0: Yes; vos.1: >99%; vos.2: Annually; vos.3: Data transfer errors are checked at secondary device(s) AND tertiary device(s); vos.4: No; vos.5: Annually; vos.6: Yes; vos.7: Between ±3% to ±6%; vos.8: Yes; vos.9: Daily; vos.10: Daily; vosea.1: Yes; vosea.2: Yes; vosea.3: No; vosea.4: No error adjustment made due to absence of testing or calibration results; wi.0: No; we.0: No; bmac.0: Yes; bmac.1: 5% or less; bmac.2: Quarterly; bmac.3: No; bmac.4: Every billing cycle; bmac.5: Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption; bmac.6: Between 3 and 5 years ago; bmac.7: Third party review includes a check on a sample of accounts; buac.0: No; umac.0: No; uuac.0: Default is used because Custom Value is selected but no value has been entered; sdhe.0: Default is used because Custom Value is selected but no value has been entered; cmi.0: Yes; cmi.1: Reactive testing conducted; cmi.2: Not recurring, but conducted within 5 years prior to audit period; cmi.3: Testing targeted to subsets of meters ie oldest meters; cmi.4: Not recurring, but conducted within 5 years prior to audit period; cmi.5: Testing targeted to subsets of meters (ie most revenue generating or customer types); cmi.6: Calculated based on most recent meter accuracy tests, but not comprehensive of all meter performance; cmi.7: No; cmi.8: Replacement upon complete failure or special circumstance (as needed); cmi.9: Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer; uc.0: Default is used because Custom Value is selected but no value has been entered; Lm.1: Derived directly from Mains inventory (GIS, ledger, etc); Lm.2: Yes; Lm.3: Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually; Lm.4: Field validation is accomplished (i.e. in daily operations or specific validation projects); Nc.1: Extracted from Services inventory (GIS, billing system, etc); Nc.2: Premise based, i.e. service connection count, location ID count; Nc.3: Yes; Nc.4: Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually; Nc.5: Field validation is accomplished for a portion of the system (i.e. in daily operations or specific validation projects); Lp.0: No; Lp.1: Derived from full mapping and customer inventory; Lp.2: Additions or subtractions are updated in the service line and meter locations inventory, but less than annually; Lp.3: Field validation is accomplished (i.e. through normal work order processes or specific validation projects); Lp.4: Policy is clear, and adherance in practice is consistent; aop.1: Not applicable, the system operates as a single pressure zone; aop.2: Collected annually during routine system flushing and/or hydrant testing; aop.3: Continuous pressure data is not collected; aop.5: Derived from hydraulic model, where model has been field calibrated in the last 5 years; cruc.0: Yes; cruc.1: Customer bill calculations have been checked to confirm the rate structure is correctly implemented; cruc.2: Rate structure has only a single volumetric rate, and this was used as the input; cruc.3: No; cruc.4: No; vpc.2: All applicable short-run marginal costs are included; vpc.3: Long-run marginal costs have been evaluated for applicability, and some but not all applicable costs are included; vpc.4: No | vos.4 | vosea.3 |  |  |  |  | bmac.2 |  |  |  |  | cmi.2, cmi.4 |  |  | Nc.5 | Lp.2 | aop.3 | cruc.4 | [61 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_NY_MARGARETVILLE VILLAGE_1974-157.xlsx | 6.0
2025-11-14 19:49:17.96 UTC | MichaelThompson | -- | -- | Aqua Pennslyvania - East Point | East Point | Pennsylvania (PA) | USA | Nick Alberici | ntalberici@aquaamerica.com | 610-645-4250 | 2024 | 2024 | 01/01/24 - 12/31/24 | 45741 | Million gallons (US) | PWSID # 3061153 |  |  | 25 | Retail | Potable Water | 3.219 | -0.065694 | 0 | 0 | 0 | 0 | 3.2847 | 1.736 | 0 | 0 | 0.00434 | 1 | 1.7403 | 1.5444 | 0.00434 | 1 | 0.035429 | 0.02 | 0.00434 | 1 | 0.044109 | 1.5002 | 1.5487 | 0.5 | 16 | 32 | No | 35 | 110 | 2400 | 14.48 | $/1000 gallons (US) | 460 | 0.2369 | 40.5656 | 0.044109 | 1.5002 | 0.00434 | 1.5487 | 638.6921 | 690.1128 | 1.9964 | 1330.8014 | VPC | 264.4442 | 7.5528 | 256.8913 | 8220.5222 | 83.0503 | 39.9183 | 43.1321 | 6.3327 | 60 | Tier III (51-70) | 1: Volume from Own Sources (VOS) | 2: Billed Metered (BMAC) | 3: Number of Service Connections (Nc) | 6 | 4 |  |  |  |  | 8 |  |  | 3 | 3 | 6 | 3 | 7 | 5 | 1 | 7 | 5 | 9 | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Once per month | Yes | Yes | Yes | Results are available but not analyzed | No | [14 empty] | No | >99% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Once per month | Once per month | Yes, written | No, but meter accuracy testing and/or electronic calibration is conducted upon request of the importing utility | No | Exporting and Importing Utility | Yes | 5% or less | Monthly | No | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | Between 3 and 5 years ago | Full billing database query and analysis of raw data to verify the summary consumption volumes | No |  |  |  | No |  |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | Yes | Reactive testing conducted | Recurring, within 5 years prior to audit period | Testing targeted to subsets of meters ie oldest meters | Recurring, within 5 years prior to audit period, but less frequently than annually | Testing targeted to subsets of meters (ie most revenue generating or customer types) | Meter accuracy test results or manufacturer specs are referenced but not analyzed and used directly in calculation | No | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | No | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | No field validation is conducted | Extracted from Services inventory (GIS, billing system, etc) | Non-premise based, i.e. meter count, customer count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | No field validation is conducted | No | Guesstimated | Customer Service Line and Meter Locations inventory is not maintained or updated |  | Policy is clear, and adherance in practice is consistent | Normally-closed boundary valves between zones have been confirmed within the past 3 years to be fully closed | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Temporary data logger(s) deployed, but limited and not capturing seasonal variation during the year | Derived from hydraulic model, where model has been field calibrated in the last 5 years | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | A non-weighted average of multiple rates was calculated | Yes, but this has not been incorporated into the volume-weighted average calculation | No | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and some but not all applicable costs are included | No | vos.10 | vosea.4 |  |  |  | weea.3 | bmac.3 |  |  |  |  | cmi.6 |  | Lm.4 | Nc.5 | Lp.1, Lp.2 | aop.4 | cruc.2 | vpc.3, vpc.4 | [17 empty] | NRW is high in East Point due to repeated flushing of system. | [42 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_PA_Aqua PA (East Point)_2002-001.xlsx | 6.0
2025-11-14 19:49:18.23 UTC | MichaelThompson | TRUE | -- | Aqua Pennslyvania - Fawn Lake | Fawn Lake | Pennsylvania (PA) | USA | Nick Alberici | ntalberici@aquaamerica.com | 610-645-4250 | 2024 | 2024 | 01/01/24 - 12/31/24 | 45737 | Million gallons (US) | PWSID # 2520037 |  |  | 1800 | Retail | Potable Water | 87.722 | -1.7902 | 0.463 | 0 | 15.642 | -0.31922 | 74.014 | 26.968 | 0 | 1.556 | 0.06742 | 1 | 28.5914 | 45.4226 | 0.06742 | 1 | 0.58212 | 0.02 | 0.06742 | 1 | 0.71696 | 44.7056 | 47.046 | 65.2 | 778 | 11.9325 | No | 15 | 100 | 64900 | 14.48 | $/1000 gallons (US) | 460 | 17.7393 | 62.469 | 0.71696 | 44.7056 | 1.6234 | 47.046 | 9936.4097 | 20564.5935 |  | 30501.0032 | VPC | [10 empty] | 1: Volume from Own Sources (VOS) | 2: Billed Metered (BMAC) | 3: Number of Service Connections (Nc) | 6 | 4 |  |  | 6 | 4 | 8 |  | 4 | 3 | 3 | 6 | 3 | 7 | 5 | 1 | 7 | 5 | 9 | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Once per month | Yes | Yes | Yes | Results are available but not analyzed | No | [14 empty] | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Once per month | Once per month | Yes, written | No, but meter accuracy testing and/or electronic calibration is conducted upon request of the importing utility | No | Exporting and Importing Utility | Yes | 5% or less | Monthly | No | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | Between 3 and 5 years ago | Full billing database query and analysis of raw data to verify the summary consumption volumes | No |  |  |  | Yes | Policy broadly addresses and there exists a collective understanding | Monitored, count available | Quarterly | Less than annually | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | Yes | Reactive testing conducted | Recurring, within 5 years prior to audit period | Testing targeted to subsets of meters ie oldest meters | Recurring, within 5 years prior to audit period, but less frequently than annually | Testing targeted to subsets of meters (ie most revenue generating or customer types) | Meter accuracy test results or manufacturer specs are referenced but not analyzed and used directly in calculation | No | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | No | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | No field validation is conducted | Extracted from Services inventory (GIS, billing system, etc) | Non-premise based, i.e. meter count, customer count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | No field validation is conducted | No | Guesstimated | Customer Service Line and Meter Locations inventory is not maintained or updated |  | Policy is clear, and adherance in practice is consistent | Normally-closed boundary valves between zones have been confirmed within the past 3 years to be fully closed | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Temporary data logger(s) deployed, but limited and not capturing seasonal variation during the year | Derived from hydraulic model, where model has been field calibrated in the last 5 years | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | A non-weighted average of multiple rates was calculated | Yes, but this has not been incorporated into the volume-weighted average calculation | No | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and some but not all applicable costs are included | No | vos.10 | vosea.4 |  |  | we.9, we.10 | weea.3 | bmac.3 |  | umac.1 |  |  | cmi.6 |  | Lm.4 | Nc.5 | Lp.1, Lp.2 | aop.4 | cruc.2 | vpc.3, vpc.4 | [60 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_PA_Aqua PA (Fawn Lake aka Lackawaxan)_1981-061.xlsx | 6.0
2025-11-14 19:49:18.50 UTC | MichaelThompson | -- | -- | Aqua Pennslyvania - Uwchlan | Uwchlan | Pennsylvania (PA) | USA | Nick Alberici | ntalberici@aquaamerica.com | 610-645-4250 | 2024 | 2024 | 01/01/24 - 12/31/24 | 45741 | Million gallons (US) | PWSID # 1150035 |  |  | 36600 | Retail | Potable Water | 979.347 | -19.9867 | 325.49 | -6.6427 | 0 | 0 | 1331.4663 | 1011.614 | 0 | 0 | 2.529 | 1 | 1014.143 | 317.3233 | 2.529 | 1 | 10.2183 | 0.01 | 2.529 | 1 | 15.2764 | 302.0469 | 319.8523 | 218 | 16745 | 76.8119 | No | 35 | 100 | 724700 | 14.48 | $/1000 gallons (US) | 460 | 165.1122 | 27.0148 | 15.2764 | 302.0469 | 2.529 | 319.8523 | 221202.174 | 138941.5732 | 1163.3561 | 361307.1033 | VPC | 51.9187 | 2.4994 | 49.4193 | 3795.9897 | 21.5075 | 13.21 | 8.2975 | 1.8293 | 59 | Tier III (51-70) | 1: Volume from Own Sources (VOS) | 2: Water Imported (WI) | 3: Billed Metered (BMAC) | 6 | 4 | 4 | 4 |  |  | 8 |  |  | 3 | 3 | 6 | 3 | 7 | 5 | 1 | 7 | 5 | 9 | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Once per month | Yes | Yes | Yes | Results are available but not analyzed | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Less frequently than monthly | Yes, written | No, but meter accuracy testing and/or electronic calibration is conducted upon request of the importing utility | No | Exporting and Importing Utility | No | >99% | Annually | Data transfer errors are checked at secondary device(s), but not to tertiary device(s) | Yes | Annually | Yes | At or within ±3% | Yes | Once per month | Once per month | Yes, written | No, but meter accuracy testing and/or electronic calibration is conducted upon request of the importing utility | No | Exporting and Importing Utility | Yes | 5% or less | Monthly | No | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | Between 3 and 5 years ago | Full billing database query and analysis of raw data to verify the summary consumption volumes | No |  |  |  | No |  |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | Yes | Reactive testing conducted | Recurring, within 5 years prior to audit period | Testing targeted to subsets of meters ie oldest meters | Recurring, within 5 years prior to audit period, but less frequently than annually | Testing targeted to subsets of meters (ie most revenue generating or customer types) | Meter accuracy test results or manufacturer specs are referenced but not analyzed and used directly in calculation | No | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | No | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | No field validation is conducted | Extracted from Services inventory (GIS, billing system, etc) | Non-premise based, i.e. meter count, customer count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | No field validation is conducted | No | Guesstimated | Customer Service Line and Meter Locations inventory is not maintained or updated |  | Policy is clear, and adherance in practice is consistent | Normally-closed boundary valves between zones have been confirmed within the past 3 years to be fully closed | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Temporary data logger(s) deployed, but limited and not capturing seasonal variation during the year | Derived from hydraulic model, where model has been field calibrated in the last 5 years | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | A non-weighted average of multiple rates was calculated | Yes, but this has not been incorporated into the volume-weighted average calculation | No | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and some but not all applicable costs are included | No | vos.10 | vosea.4 | wi.10 | wiea.3 |  | weea.3 | bmac.3 |  |  |  |  | cmi.6 |  | Lm.4 | Nc.5 | Lp.1, Lp.2 | aop.4 | cruc.2 | vpc.3, vpc.4 | [60 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_PA_Aqua PA (Uwchlan)_1990-050.xlsx | 6.0
2025-11-14 19:49:18.78 UTC | MichaelThompson | TRUE | -- | Dublin Borough (D-2000-011 CP-3) | Dublin Borough | Pennsylvania (PA) | United States of America | Matthew Bailor P.E. | mbailor@gilmore-assoc.com | 215 345-4330 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45742 | Million gallons (US) | 1090107 | n/a | n/a | 2200 | Retail | Potable Water | 43.0656 | 0 | 0 | 0 | 0 | 0 | 43.0656 | 38.2681 | 0 | 0 | 0.034 | 2 | 38.3021 | 4.7635 | 0.09567 | 1 | 0 |  | 0.09567 | 1 | 0.19134 | 4.5722 | 4.7975 | 6.2 | 1421 | 229.1935 | No | 50 | 60 |  | 6.9211 | $/1000 gallons (US) | 2637.3734 | 7.6128 | 14.6776 | 0.19134 | 4.5722 | 0.034 | 4.7975 | 1324.2939 | 12058.5054 |  | 13382.7993 | VPC | [9 empty] | TBD |  |  |  | 7 | 4 |  |  |  |  | 7 |  |  | 4 | 3 | 2 | 3 | 8 | 8 | 1 | 6 | 1 |  | vos.0: Yes; vos.1: >99%; vos.2: Not applicable due to no electronic signal output (i.e. to SCADA); vos.5: Less than annual but within last 5 years; vos.6: Yes; vos.7: Between ±3% to ±6%; vos.8: No; vos.9: Daily; vos.10: More frequently than monthly, but not every day; vosea.1: Yes; vosea.2: Yes; vosea.3: Yes; vosea.4: Results are available but not analyzed; wi.0: No; we.0: No; bmac.0: Yes; bmac.1: 5% or less; bmac.2: Quarterly; bmac.3: Yes; bmac.4: Every billing cycle; bmac.5: Sum total only; bmac.6: More than 5 years ago, or not sure; buac.0: No; umac.0: No; uuac.0: A system specific volume has been entered; uuac.1: Examples known, but no complete inventory; uuac.2: Each event is documented; uuac.3: By a mix of some guesstimation and some event-specific estimates; sdhe.0: Default is used because Custom Value is selected but no value has been entered; cmi.0: Yes; cmi.1: Reactive testing conducted; cmi.2: Not recurring, but conducted within 5 years prior to audit period; cmi.3: Proactive - representative sample (for small meters); cmi.4: Not recurring, but conducted within 5 years prior to audit period; cmi.5: Testing targeted to subsets of meters (ie most revenue generating or customer types); cmi.6: Guesstimated without any customer meter testing data as a reference; cmi.7: No; cmi.8: Replacement upon complete failure or special circumstance (as needed); cmi.9: Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer; uc.0: Default is used because Custom Value is selected but no value has been entered; Lm.1: Derived directly from Mains inventory (GIS, ledger, etc); Lm.2: No; Lm.3: Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually; Lm.4: Field validation is accomplished (i.e. in daily operations or specific validation projects); Nc.1: Extracted from Services inventory (GIS, billing system, etc); Nc.2: Non-premise based, i.e. meter count, customer count; Nc.3: Yes; Nc.4: Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually; Nc.5: Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects); Lp.0: No; Lp.1: Guesstimated; Lp.2: Customer Service Line and Meter Locations inventory is not maintained or updated; Lp.4: Policy is clear, but adherence in practice is uncertain; aop.1: Not applicable, the system operates as a single pressure zone; aop.2: Collected annually during routine system flushing and/or hydrant testing; aop.3: Continuous pressure data is not collected; aop.5: Calculated from field data as a simple average; cruc.0: Yes; cruc.1: Customer bill calculations have not been checked to confirm the rate structure is correctly implemented; cruc.2: Rate structure has only a single volumetric rate, and this was used as the input; cruc.3: Yes, but this has not been incorporated into the volume-weighted average calculation; cruc.4: No; vpc.2: All applicable short-run marginal costs are included; vpc.3: Long-run marginal costs have not been evaluated for applicability, and are not included; vpc.4: No | vos.5 | vosea.4 |  |  |  |  | bmac.2, bmac.5 |  |  | uuac.1 |  | cmi.6 |  | Lm.2 | Nc.2 | Lp.1, Lp.2 | aop.3 | cruc.1 | [61 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_PA_Dublin Borough_2000-011.xlsx | 6.0
2025-11-14 19:49:19.05 UTC | MichaelThompson | -- | -- | Morrisville Municipal Authority | Morrisville | Pennsylvania (PA) | United States | Chris T. Harris | mmawtp@verizon.net | 215-295-4547 | 2024 | Calender | 01/01/24 - 12/31/24 | March 20,2024 | Million gallons (US) | PA 1090037 |  |  | 13342 | Retail | Potable Water | 1246.751 | 0 | 0 | 0 | 421.527 | 0 | 825.224 | 408.44 |  | 34.75 | 102.565 | 2 | 545.755 | 279.469 | 1.0211 | 1 | 9.0447 | 0.02 | 1.0211 | 1 | 11.0869 | 268.3821 | 416.784 | 48 | 4261 | 88.7708 | No | 45 | 55 | 3561190 | 3.98 | $/1000 gallons (US) | 643 | 23.5117 | 15.1175 | 11.0869 | 268.3821 | 137.315 | 416.784 | 41759.2917 | 172569.6942 | 88293.545 | 302622.531 | VPC | 179.6922 | 7.1286 | 172.5636 | 15318.6134 | 50.3002 | 9.8004 | 40.4998 | 11.4148 | 54 | Tier III (51-70) | 1: Length of Mains (Lm) | 2: Customer Retail Unit Charge (CRUC) | 3: Volume from Own Sources (VOS) | 8 | 8 |  |  | 6 | 4 | 7 |  | 7 | 4 | 3 | 3 | 3 | 1 | 6 | 6 | 6 | 1 | 4 | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Annually | Yes | At or within ±3% | No | Daily | More frequently than monthly, but not every day | Yes | No | No | No error adjustment made due to absence of testing or calibration results | No |  | Not applicable due to no electronic signal output (i.e. to SCADA) | [8 empty] | Yes, written |  |  |  | Yes | >99% | Not applicable due to no electronic signal output (i.e. to SCADA) |  |  | Annually | Yes | At or within ±3% | Yes | Once per month | Once per month | Yes, written | No, but meter accuracy testing and/or electronic calibration is conducted upon request of the importing utility | No | Exporting and Importing Utility | Yes | 5% or less | Quarterly | No | Annually | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | More than 5 years ago, or not sure |  | No |  |  |  | Yes | Policy includes specific exemptions | Monitored, count available | Quarterly | Annually | A system specific volume has been entered | Examples known, but no complete inventory | Documentation exists, but not specific to each event | By a mix of some guesstimation and some event-specific estimates | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | Yes | Reactive testing conducted | No testing conducted, but at least 10% of meter stock has been replaced within two years of the audit period |  | No proactive large meter testing activity to date | Testing targeted to subsets of meters (ie most revenue generating or customer types) | No test results were used, but at least 50% of meter stock has been replaced within two years of the audit period | No | Replacement upon complete failure or special circumstance (as needed) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Guesstimated |  | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), but less than annually | No field validation is conducted | Extracted from Services inventory (GIS, billing system, etc) | Non-premise based, i.e. meter count, customer count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), but less than annually | Field validation is accomplished for a portion of the system (i.e. in daily operations or specific validation projects) | No | Derived from full mapping and customer inventory | Additions or subtractions are updated in the service line and meter locations inventory, but less than annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, but adherence in practice is uncertain | Not applicable, the system operates as a single pressure zone | Collected only if there are low pressure complaints, or new development requests | Continuous pressure data is not collected |  | Calculated from field data as a simple average | Yes | Customer bill calculations have not been checked to confirm the rate structure is correctly implemented | Guesstimated | Yes, but this has not been incorporated into the volume-weighted average calculation | No | A non-weighted average of multiple sources was calculated | All applicable short-run marginal costs are included | Long-run marginal costs have not been evaluated for applicability, and are not included | No | vos.10 | vosea.2 |  |  | we.9, we.10 | weea.3 | bmac.2 |  | umac.4 | uuac.1 |  | cmi.4 |  |  | Nc.4 | Lp.2, Lp.4 | aop.3 | cruc.1, cruc.2 | vpc.1 | [60 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_PA_Morrisville Municipal Authority_1974-072.xlsx | 6.0
2025-11-14 19:49:19.33 UTC | MichaelThompson | -- | -- | PAW - 560 Nazareth | Nazareth | Pennsylvania (PA) | USA | James Baer | james.baer@amwater.com | 610-842-3118 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45712 | Million gallons (US) | 3480055 | n/a | n/a | 39194 | Retail | Potable Water | 788.766 | -2.3734 | 0 | 0 | 0 | 0 | 791.1394 | 657.622 | 0 | 14.062 | 16.373 | 2 | 688.057 | 103.0824 | 0.277 | 2 | 13.7078 | 0.02 | 0.553 | 2 | 14.5378 | 88.5446 | 133.5174 | 158.2 | 10633 | 67.2124 | No | 19.3 | 94.9 | 3768675 | 15.99 | $/1000 gallons (US) | 303.57 | 94.9896 | 24.4753 | 14.5378 | 88.5446 | 30.435 | 133.5174 | 227958.3241 | 26879.4786 | 9239.1529 | 264076.9557 | VPC | 26.5605 | 3.7459 | 22.8146 | 1533.4254 | 23.9667 | 21.4388 | 2.5279 | 0.93215 | 93 | Tier V (91-100) | 1: Customer Metering Inaccuracies (CMI) | 2: Billed Metered (BMAC) | 3: Unauthorized Consumption (UC) | 10 | 10 |  |  |  |  | 9 |  | 10 | 10 | 8 | 4 | 10 | 10 | 10 | 10 | 8 | 10 | 10 | Yes | >99% | At least semi-annually | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | At least semi-annually | Yes | At or within ±3% | Yes | Continuous | Daily | Yes | Yes | Yes | Yes, results are analyzed and incorporated | No | [14 empty] | No | [14 empty] | Yes | 5% or less | Monthly | Yes | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | Within last 3 years | Full billing database query and analysis of raw data to verify the summary consumption volumes | No |  |  |  | Yes | Policy includes specific exemptions | Monitored, count available | Monthly or more frequently | Each billing cycle | A system specific volume has been entered | Complete inventory exists | Each event is documented | Entirely from event-specific estimates | A system specific volume has been entered | Estimation derived from a specific analysis at the account level to identify erroneous unbilled consumption | All meter multipliers have been analyzed to confirm multiplier conversion in the billing system is correct | Policy is clear, and adherance in practice is consistent | Detailed analysis conducted within 3 years of the audit period on stuck meters, extended estimations, & miscoded multipliers | Yes | Reactive testing conducted | No testing conducted, but at least 10% of meter stock has been replaced within two years of the audit period | Proactive - representative sample (for small meters) | Not recurring, last testing effort occurred more than 5 years prior to audit period | Proactive - all large meters are on a testing schedule | Meter accuracy test results or manufacturer specs are referenced but not analyzed and used directly in calculation | Yes | Replacement upon complete failure or special circumstance (as needed) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | A system specific volume has been entered | Estimation for custom volume derived from system-wide study | Limited investigation performed and documented for unauthorized consumption, beyond reactively discovered events | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | No | Derived from full mapping and customer inventory | Additions or subtractions are updated in the service line and meter locations inventory, at least annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, and adherance in practice is consistent | Normally-closed boundary valves between zones have been confirmed within the past 3 years to be fully closed | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Year-round data collection via permanent monitoring | Derived from hydraulic model, where model has been field calibrated in the last 5 years | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | A volume-weighted average of all rates was calculated | No | Yes | Only one source of water exists, which was the basis for the input derivation | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and all applicable costs are included | Yes | [6 empty] | bmac.2 |  |  |  |  | cmi.4 | uc.2 |  |  |  | aop.3 | [62 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_PA_PAWC (Blue Mnt Nazereth Dist # 560)_1977-047.xlsx | 6.0
2025-11-14 19:49:19.63 UTC | MichaelThompson | -- | -- | PAW - 510 Norristown | Norristown | Pennsylvania (PA) | USA | James Baer | james.baer@amwater.com | 610-842-3118 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45713 | Million gallons (US) | 1460046 | n/a | n/a | 117305 | Retail | Potable Water | 3344.375 | 165.3113 | 14.087 | 0.070085 | 12.518 | 0.062279 | 3180.6249 | 2357.3 | 0 | 5.991 | 76.75 | 2 | 2440.041 | 740.5839 | 17.752 | 2 | 48.2304 | 0.02 | 6.65 | 2 | 72.6324 | 667.9515 | 823.3249 | 390.8 | 32219 | 82.4437 | No | 19.2 | 80.3 | 12351641 | 15.99 | $/1000 gallons (US) | 1115.12 | 229.3696 | 19.5043 | 72.6324 | 667.9515 | 82.741 | 823.3249 | 1159573.8511 | 744846.025 | 92266.1439 | 1996686.02 | VPC | 62.9752 | 6.1763 | 56.7989 | 4682.7123 | 59.1086 | 35.9904 | 23.1182 | 2.9121 | 89 | Tier IV (71-90) | 1: Customer Metering Inaccuracies (CMI) | 2: Volume from Own Sources (VOS) | 3: Billed Metered (BMAC) | 9 | 10 | 6 | 9 | 6 | 6 | 9 |  | 10 | 10 | 8 | 4 | 10 | 10 | 10 | 10 | 8 | 10 | 10 | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | At least semi-annually | Yes | At or within ±3% | Yes | Continuous | Daily | Yes | Yes | Yes | Yes, results are analyzed and a 'no-adjustment' was determined | Yes | >99% | Not applicable due to no electronic signal output (i.e. to SCADA) | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | At or within ±3% | Yes | Once per month | Once per month | Yes, written | Yes, and stipulated frequency as annual | Yes, results are analyzed and incorporated | Exporting and Importing Utility | Yes | >99% | Not applicable due to no electronic signal output (i.e. to SCADA) | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | Between ±3% to ±6% | Yes | Once per month | Once per month | Yes, written | Yes, and stipulated as less frequent than annual | Yes, results are analyzed and incorporated | Exporting and Importing Utility | Yes | 5% or less | Monthly | Yes | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | Within last 3 years | Full billing database query and analysis of raw data to verify the summary consumption volumes | No |  |  |  | Yes | Policy includes specific exemptions | Monitored, count available | Monthly or more frequently | Each billing cycle | A system specific volume has been entered | Complete inventory exists | Each event is documented | Entirely from event-specific estimates | A system specific volume has been entered | Estimation derived from a specific analysis at the account level to identify erroneous unbilled consumption | All meter multipliers have been analyzed to confirm multiplier conversion in the billing system is correct | Policy is clear, and adherance in practice is consistent | Detailed analysis conducted within 3 years of the audit period on stuck meters, extended estimations, & miscoded multipliers | Yes | Reactive testing conducted | No testing conducted, but at least 10% of meter stock has been replaced within two years of the audit period | Proactive - representative sample (for small meters) | Not recurring, last testing effort occurred more than 5 years prior to audit period | Proactive - all large meters are on a testing schedule | Calculated based on most recent meter accuracy tests, but not comprehensive of all meter performance | Yes | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | A system specific volume has been entered | Estimation for custom volume derived from system-wide study | Limited investigation performed and documented for unauthorized consumption, beyond reactively discovered events | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | No | Derived from full mapping and customer inventory | Additions or subtractions are updated in the service line and meter locations inventory, at least annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, and adherance in practice is consistent | Normally-closed boundary valves between zones have been confirmed within the past 3 years to be fully closed | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Year-round data collection via permanent monitoring | Derived from hydraulic model, where model has been field calibrated in the last 5 years | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | A volume-weighted average of all rates was calculated | No | Yes | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and all applicable costs are included | Yes | vos.2 |  | wi.9, wi.10 | wiea.2 | we.9, we.10 | weea.2 | bmac.2 |  |  |  |  | cmi.4 | uc.2 |  |  |  | aop.3 | [62 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_PA_PAWC (Norristown District #510)_1966-100.xlsx | 6.0
2025-11-14 19:49:19.90 UTC | MichaelThompson | -- | -- | Quakertown Water Department (1090082) | Quakertown | Pennsylvania (PA) | USA | David "Butch" Erwin | derwin@quakertown.org | 215-536-5004 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45369 | Million gallons (US) | 1090082 | Matthew Mercuri | mmercuri@rmsenvironmental.com | 14800 |  | Potable Water | 367.113 | 0.36675 | 0 | 0 | 0 | 0 | 366.7463 | 293.482 |  | 22.517 | 0.1 | 2 | 316.099 | 50.6473 | 0.063 | 2 | 0.1 |  | 0.001 | 2 | 0.164 | 50.4833 | 73.2643 | 41 | 4271 | 104.1707 | No | 40 | 68.5 | 2934184 | 5.81 | $/1000 gallons (US) | 711.585 | 27.631 | 17.7245 | 0.164 | 50.4833 | 22.617 | 73.2643 | 916.5105 | 35923.1261 | 16093.9179 | 52933.5545 | VPC | 32.4888 | 0.1052 | 32.3836 | 3373.4216 | 8.6255 | 0.21459 | 8.4109 | 1.827 | 93 | Tier V (91-100) | 1: Volume from Own Sources (VOS) | 2: Billed Metered (BMAC) | 3: Unauthorized Consumption (UC) | 9 | 10 |  |  |  |  | 9 |  | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | Yes | >99% | Annually | Data transfer errors are checked at secondary device(s), but no tertiary device(s) exist | Yes | Annually | Yes | At or within ±3% | Yes | Continuous | Daily | Yes | Yes | Yes | Yes, results are analyzed and incorporated | No | [14 empty] | No | [14 empty] | Yes | 5% or less | Monthly | Yes | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | Within last 3 years | Third party review includes a check on a sample of accounts | No |  |  |  | Yes | Policy includes specific exemptions | Monitored, count available | Monthly or more frequently | More than annually, but less than every billing cycle | A system specific volume has been entered | Majority identified and tracked | Each event is documented | Entirely from event-specific estimates | A system specific volume has been entered | Estimation derived from a specific analysis at the account level to identify erroneous unbilled consumption | All meter multipliers have been analyzed to confirm multiplier conversion in the billing system is correct | Policy is clear, and adherance in practice is consistent | Detailed analysis conducted within 3 years of the audit period on stuck meters, extended estimations, & miscoded multipliers | Yes | Reactive testing conducted | Ongoing, conducted annually | Proactive - representative sample (for small meters) | Ongoing, conducted annually | Proactive - all large meters are on a testing schedule | Calculated based on most recent meter accuracy tests, comprehensive of all meter performance | Yes | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | A system specific volume has been entered | Estimation for custom volume extrapolated from study, sampling a portion of the system | Limited investigation performed and documented for unauthorized consumption, beyond reactively discovered events | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | No | Derived from full mapping and customer inventory | Additions or subtractions are updated in the service line and meter locations inventory, at least annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, and adherance in practice is consistent | Normally-closed boundary valves between zones have been confirmed within the past 3 years to be fully closed | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions, plus locations inside the zone(s) representing the full pressure profile | Year-round data collection via permanent monitoring | Calculated from field data as a weighted average, compliant with methods described in the M36 Manual | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | A volume-weighted average of all rates was calculated | Yes, and this has been incorporated into the volume-weighted average calculation | Yes | Multiple sources of water exist, and a volume-weighted average was calculated for all sources | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and all applicable costs are included | Yes | vos.2, vos.5 | [5 empty] | bmac.2, bmac.7 |  | umac.4 | uuac.1 |  |  | uc.1, uc.2 |  |  |  | aop.5 | [62 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_PA_Quakertown Borough_2000-064.xlsx | 6.0
2025-11-14 19:49:20.16 UTC | MichaelThompson | -- | -- | Shoemakersville Borough | Shoemakersville | Pennsylvania (PA) | USA | Paul Gruber | pgruber@shoeyboro.org | 610-562-8030 | 2024 | Calendar | 01/01/24 - 12/31/24 | 45754 | Million gallons (US) | 3060100 | n/a | n/a | 1360 | Hybrid Wholesale + Retail | Potable Water | 36.164 | -0.090637 | 0 | 0 | 0.012 | -3.0075e-05 | 36.2426 | 21.478 | 0 | 10.855 | 0.053695 | 1 | 32.3867 | 3.8559 | 0.053695 | 1 | 0.081035 | 0.0025 | 0.053695 | 1 | 0.18843 | 3.6675 | 14.7646 | 12 | 735 | 61.25 | No | 16 | 68 | 298949 | 13 | $/1000 gallons (US) | 120.97 | 4.7623 | 17.7517 | 0.18843 | 3.6675 | 10.9087 | 14.7646 | 2099.1455 | 443.6558 | 1319.6248 | 3862.4262 | VPC | 14.373 | 0.70236 | 13.6706 | 837.3257 | 3.4596 | 2.856 | 0.60361 | 0.7701 | 47 | Tier II (26-50) | 1: Volume from Own Sources (VOS) | 2: Customer Metering Inaccuracies (CMI) | 3: Unbilled Metered (UMAC) | 3 | 4 |  |  | 1 | 3 | 7 |  | 4 | 3 | 3 | 3 | 3 | 6 | 5 | 6 | 5 | 9 | 9 | Yes | >95 - 99% | Less than annual but within last 5 years | Data transfer errors are not checked, or not sure | Yes | None, or Not within last 5 years |  |  | No | Daily | Once per month | Yes | No | No | Results are available but not analyzed | No | [14 empty] | Yes | >99% | Less than annual but within last 5 years | Data transfer errors are not checked, or not sure | No | None, or Not within last 5 years |  |  | No | Once per month | Regular review not conducted / Not sure | Yes, written | No | No | Exporting and Importing Utility | Yes | 5% or less | Quarterly | No | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | More than 5 years ago, or not sure |  | No |  |  |  | Yes | Policy broadly addresses and there exists a collective understanding | Monitored, count available | Monthly or more frequently | Each billing cycle | Default is used because Custom Value is selected but no value has been entered |  |  |  | Default is used because Custom Value is selected but no value has been entered |  |  |  |  | Yes | Reactive testing conducted | No testing conducted, but at least 10% of meter stock has been replaced within two years of the audit period |  | No proactive large meter testing activity to date |  | Meter accuracy test results or manufacturer specs are referenced but not analyzed and used directly in calculation | No | Annual proactive replacement of subset of meters (i.e. by age or throughput) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | Default is used because Custom Value is selected but no value has been entered |  |  | Derived directly from Mains inventory (GIS, ledger, etc) | No | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), but less than annually | No field validation is conducted | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | No | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for a portion of the system (i.e. in daily operations or specific validation projects) | No | Derived from full mapping and customer inventory | Additions or subtractions are updated in the service line and meter locations inventory, but less than annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, and adherance in practice is consistent | Not applicable, the system operates as a single pressure zone | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions only (i.e. supply entry points, PRVs, booster stations) | Temporary data logger(s) deployed, but limited and not capturing seasonal variation during the year | Loose estimate inferred from field measurements, but no analysis nor calculations performed | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | Rate structure has only a single volumetric rate, and this was used as the input | No | No | Only one source of water exists, which was the basis for the input derivation | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and all applicable costs are included | No | vos.5 | vosea.4 |  |  | we.10 | weea.2 | bmac.2 |  | umac.1 |  |  | cmi.4 |  | Lm.3 | Nc.3 | Lp.2 | aop.5 | cruc.4 | vpc.4 | 14 | 0.7 | 13.7 | 837 | [56 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_PA_SHOEMAKERSVILLE BOROUGH_1990-007.xlsx | 6.0
2025-11-14 19:49:20.43 UTC | MichaelThompson | -- | -- | Warminster Municipal Authority | Warminster | Pennsylvania (PA) | United States | Thomas Campion | tomc@warminsterauthority.com | 2156753301 | 2024 | Calendar | 01/01/24 - 12/31/24 |  | Million gallons (US) | 1090069 | n/a | n/a |  | Retail | Potable Water | 135.674 | -0.13581 | 893.914 | -0.89481 | 0 | 0 | 1030.6186 | 935.643 | 0 | 29.581 | 47.56 | 2 | 1012.784 | 17.8346 | 2.339 | 2 | 1 | 0.01 | 0.5 | 2 | 3.839 | 13.9956 | 94.9756 | 173.7 | 10725 | 61.7444 | No | 40 | 75 | 5746700 | 5.61 | $/1000 gallons (US) | 2500 | 86.4459 | 22.0828 | 3.839 | 13.9956 | 77.141 | 94.9756 | 21441.4785 | 34989.0465 | 192852.5 | 249283.0251 | VPC | 4.5559 | 0.98068 | 3.5752 | 220.7493 | 5.2616 | 1.9992 | 3.2624 | 0.1619 | 74 | Tier IV (71-90) | 1: Water Imported (WI) | 2: Customer Metering Inaccuracies (CMI) | 3: Volume from Own Sources (VOS) | 5 | 9 | 5 | 6 |  |  | 9 |  | 10 | 8 | 8 | 6 | 10 | 10 | 10 | 10 | 9 | 7 | 9 | Yes | >99% | Less than annual but within last 5 years | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | At or within ±3% | Yes | Daily | Daily | Yes | Yes | No | Yes, results are analyzed and incorporated | Yes | >99% | Less than annual but within last 5 years | Data transfer errors are checked at secondary device(s) AND tertiary device(s) | Yes | Less than annual but within last 5 years | Yes | At or within ±3% | Yes | Continuous | Daily | Yes, written | Yes, and stipulated as less frequent than annual | Yes, results are analyzed and a 'no-adjustment' was determined | Exporting and Importing Utility | No | [14 empty] | Yes | 5% or less | More frequently than monthly | Yes | Every billing cycle | Totals grouped by use type or customer class and specific accounts flagged for anomalous consumption | Within last 3 years | Third party review includes a check on a sample of accounts | No |  |  |  | Yes | Policy includes specific exemptions | Monitored, count available | Monthly or more frequently | Each billing cycle | A system specific volume has been entered | Majority identified and tracked | Each event is documented | Entirely from event-specific estimates | A system specific volume has been entered | Estimation derived from a specific analysis at the account level to identify erroneous unbilled consumption | All meter multipliers have been analyzed to confirm multiplier conversion in the billing system is correct | Policy is clear, and adherance in practice is consistent | Detailed analysis conducted within 3 years of the audit period on stuck meters, extended estimations, & miscoded multipliers | Yes | Reactive testing conducted | No testing conducted, but at least 10% of meter stock has been replaced within two years of the audit period |  | Not recurring, but conducted within 5 years prior to audit period | Testing targeted to subsets of meters (ie most revenue generating or customer types) | No test results were used, but at least 50% of meter stock has been replaced within two years of the audit period | No | Replacement upon complete failure or special circumstance (as needed) | Records are kept for meter installations, and they include data on installation date, type, size, and manufacturer | A system specific volume has been entered | Estimation for custom volume extrapolated from study, sampling a portion of the system | Limited investigation performed and documented for unauthorized consumption, beyond reactively discovered events | Derived directly from Mains inventory (GIS, ledger, etc) | Yes | Additions or subtractions are updated in the mains inventory (GIS, ledger, etc), at least annually | Field validation is accomplished (i.e. in daily operations or specific validation projects) | Extracted from Services inventory (GIS, billing system, etc) | Premise based, i.e. service connection count, location ID count | Yes | Additions or subtractions are updated in the service line inventory (GIS, billing system, etc), at least annually | Field validation is accomplished for the entire system (i.e. in daily operations or specific validation projects) | No | Derived from full mapping and customer inventory | Additions or subtractions are updated in the service line and meter locations inventory, at least annually | Field validation is accomplished (i.e. through normal work order processes or specific validation projects) | Policy is clear, and adherance in practice is consistent | Normally-closed boundary valves between zones have been confirmed within the past 3 years to be fully closed | Collected annually during routine system flushing and/or hydrant testing | At zone boundary conditions, plus locations inside the zone(s) representing the full pressure profile | Year-round data collection via permanent monitoring | Calculated from field data as a weighted average, compliant with methods described in the M36 Manual | Yes | Customer bill calculations have been checked to confirm the rate structure is correctly implemented | A volume-weighted average of all rates was calculated | Yes, but this has not been incorporated into the volume-weighted average calculation | No | Unit costs for the most expensive source utilized based on utility's discretion | All applicable short-run marginal costs are included | Long-run marginal costs have been evaluated for applicability, and some but not all applicable costs are included | No | vos.2, vos.5 | vosea.3 | wi.2, wi.5 | wiea.2 |  |  | bmac.7 |  |  | uuac.1 |  | cmi.4 | uc.1, uc.2 |  |  |  | aop.5 | cruc.3 | vpc.3, vpc.4 | [60 empty] | C:/Users/MichaelThompson/Documents/Compliance/Water Audit/AWWA_FWAS_R_helper/Downloads_v6/WA_CY2024_PA_Warminster Municipal Authority_2000-019.xlsx | 6.0